## Draft WBBROC Civil APAM
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
2 | A: Notes: WSAA Product Specification WSAA Product Specifications are available from www.wsaa.asn.au . Section 4 of the WSAA Product Specifications is for “Agency or Project Specific Requirements”. The SEQ requirements are specified below. Manufacturer/Supplier Products may be sourced from alternative Suppliers than those listed provided that the products are manufactured by a Manufacturer whose name, and the products’ trade name, appear on the list. Size Range Size ranges need to be read in conjunction with the relevant clauses of the SEQ versions of the WSAA Codes (e.g. Water Supply Code Clause 3.1.1; Sewerage Code Clause 10.6; Pressure Sewerage Code Clause 4.5.3.1; etc.) Blank Cells In the five columns under the service provider’s names cells that are blank indicate that the product listed on that row are acceptable to the service provider. ‘Use is subject to acceptance by SP’ Contact the service provider to determine if the use of this product is acceptable in the proposed circumstance. ‘Flange’ All flanges used for pressure systems shall be PN16 or PN35 complying with AS4087.
3 | A: Category: SEWERAGE PIPES AND FITTINGS - NON PRESSURE
4 | PVC-U pipe and fittings - DWV system | 230 4.1 - Plain Wall 4.2 - Elastomeric Seal 4.3 - Stiffness as per 230.2.(c) or as required by SP 4.4 - RRJ @ SBR & EPDM | Iplex | DWV PIPE | DN100 150 225 300 375 | Plain wall only accepted | DN100 at SN10, DN150 and larger at SN8 and Fittings at SN8 minimum
5 | C: Vinidex; D: DWV SEWER
6 | C: Viadux; D: D-FLO
7 | C: Micron Pipelines; D: Micron Pipelines; E: DN100 - DN300
8 | C: Pipemakers; D: Pipemakers
9 | A: PVC-U Pressure pipe Sewer using Standard DWV Junctions; B: 211 4.1 - PN12 4.2 - Deep Sewers or Minimum Cover 4.3 - Standard Packaging & Delivery 4.4 - Series 1 4.5 - RRJ @ SBR & EPDM; C: Iplex; E: DN150 225 300; K: Mandatory for sewers deeper than 3 metres and for sewers with minimum cover All details to be confirmed with SP
10 | C: Vinidex
11 | C: Viadux
12 | A: DI pipe; B: 202S 4.1 – PN16 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – Polyurethane lining 4.4 – Restrained Joints on Zinc/Bitumen coated pipe 4.5 – Zinc/Bitumen coating or Polyurethane coating 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on all DI pipes unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment; C: VonRoll / Reece; D: Ducpur/ Ecopur; E: DN80 - 700; F: Polyurethane internal protection
13 | B: 200 and WSAA TN6 4.1 - PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – CAC cement lining 4.4 – Zinc/Bitumen coating 4.5 - By design 4.6 – SBR and EPDM 4.7 - PE sleeving is required on all DI pipes unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment; C: Viadux; D: Tytonxtreme; E: DN100 - 750; F: CAC cement lining; K: NOT ACCEPTED BY SP
14 | C: Crevet / Iplex; D: Irontite; E: DN100 - 750
15 | C: Saint-Gobain; D: Integral Zinalium; E: DN100 – 750; K: Use is subject to acceptance by SP
16 | A: Steel pipe; B: 203 4.1 – By design and PN16 min 4.2 – SEQ Code nominal DN’s 4.3 – Seal coat not required for sewage 4.4 – Extra protection by design 4.5 – Joints by design to SEQ Code Standards; C: Steel Mains; D: Sintapipe; F: Internal lining would be required, either Epoxy or Sintaline
17 | A: Polypropylene (PP) pipe; B: 240 4.1 - Type B - ID Series 4.2 - SN10,000 4.3 - RRJ @ SBR & EPDM; C: Vinidex; D: SewerPRO; E: DN150 - 900
18 | C: Iplex; D: SewerMAX; E: DN225 - 600
19 | C: Enviropipes; D: EnviroPipe; E: DN150 - 900; K: Use is subject to acceptance by SP
20 | A: PE pipe - NuSewers; B: 207 4.1 - Minimum PN8 SDR21 PE100 4.2 - Gravity Sewer fully welded 4.3 - Pipes lengths for DN160 and larger with coils accepted for DN110 4.4 - External colour light grey Solid or Striped with Internal colour white or light colour, see POP203 4.5 - PE100 only; C: Iplex; D: POLIplex; E: DN110 160 250 315 400 500 630 800 1000 1200
21 | C: Vinidex; D: Sewertech
22 | C: DMG; D: Hi-Vis
23 | C: Viadux
24 | C: Poly Pipe; D: SewerFlex
25 | C: Enviropipes; D: Enviropressure
26 | A: PE fittings - Moulded; B: 208 4.1 - PN10 preferred 4.2 - Electrofusion or butt welding 4.3 - Couplings and Saddles 4.4 - Bolting Flanges not required. 4.5 - Elastomeric Seals not permitted And Electrofusion fitting Standards AS4129, EN1555, EN12201, EN13244-4; C: George Fischer / Ipex; F: Electrofusion fitting to be long type.
27 | C: Friatec / Vinidex
28 | C: Plasson; D: Lightfit
29 | C: Agru; D: AGRU
30 | C: Fusion Group/FusionPlast; D: Fusamatic; E: Up to DN630; K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP.
31 | C: NUPIGECO; D: Elofit; E: DN110 to DN630
32 | A: PE fittings - Fabricated; B: 216 4.1 - PN10 preferred 4.2 - Electrofusion or butt welding Including Sweep Bends, MH Connectors, Sediment Traps, Tee and Bends for drop pipes and Sweep Junctions.; C: Vinidex; F: Electrofusion fitting to be long type. PE MH connectors shall have Hydrophilic seals both sides of puddle flange.
33 | C: Iplex
34 | A: VC pipe; B: 231 4.1 - DN100/150 Crushing Strength 34, DN225 and larger Class 160 4.2 - Sp-Soc and Sleeve Coupling 4.3 - All seal materials accepted; C: Hepworth; D: Supersleeve; E: DN100-1200; K: May only be used as jacking pipes
35 | C: Steinzeug Keramo; D: Keramo
36 | C: Naylor / Rocla; D: Denlok
37 | A: DI IO bends or X Drop fitting; B: 201 4.1 - Sp-Soc ends to serve PVC-U DWV pipe 4.2 - Refer Standard drawings 4.3 - Standard RRJ for accept PVC-U DWV pipe 4.4 - SBR & EPDM 4.5 - Thermal-bonded polymeric coated and lined; C: Crevet; F: All Di fittings to be wrapped; K: NOT ACCEPTED BY SP
38 | C: Viadux
39 | A: Metal-banded flexible coupling; B: 235 4.1 - Need for adaptor bushes where difference between OD of pipe and ID of coupling greater than 16 mm 4.2 - Metal band and bolts shall be min SS316; C: Flex-Seal; D: Flex-Seal; E: Up to DN600
40 | C: DEKS; D: DEKS shear banded coupling; E: DN100 to DN225
41 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; C: Viadux; D: Gibault - Ezigib & Varigib; F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
42 | C: Crevet; D: Gibault & Universal
43 | C: AVK; D: Gibault & Universal
44 | C: Viking Johnson; D: MaxiFit & QuickFit
45 | C: Derwent
46 | C: DEKS; D: DEKS FLEXI-GIB; E: DN80 to DN600
47 | C: Daemco; D: Reinoversal; E: Up to DN 600
| A | B | C | D | E | F | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
48 | A: Reinforced Concrete pipe; B: 233 4.1 - Class 4 4.2 - Bends not permitted 4.3 - In corrosive soils coat external face with 250 micron DFT High Build Epoxy 4.4 - Lifting holes not permitted 4.5 - 2.0 mm PE sheet Factory cast-in liner with Invert overlapped but not welded 4.6 - No additional cover 4.7 - SBR & EPDM; C: Rocla; K: Use is subject to acceptance by SP
49 | C: Humes
50 | A: Polycrete pipe; B: No WSA-PS 4.1 - Class to suit design 4.2 - Bends not permitted 4.3 - Compliance with ASTM D 6783, DIN 54815-1 and DIN 54815-2 4.4 - SBR and EPDM Sewer Pipe and Jacking Pipe approved; C: Iplex; D: Meyer pipe; E: DN200 to 2600; K: Use is subject to acceptance by SP Coupling Grade 316 Stainless Steel (min.)
51 | C: Global Pipe; D: Al Watani
52 | CC-GRP (centrifugally cast) pipe and Fittings - Sewer Pipe | 237S 4.1 - PN1 4.2 - SN10,000 minimum 4.3 - Soc-Sp RRJ 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | Sewer Pipe | Use is subject to acceptance by SP
53 | FW-GRP (filament wound) pipe and Fittings - Sewer Pipe | 205S 4.1 - As per product 4.2 - PN1 4.3 - SN10,000 minimum 4.4 - Bends, T-piece, Y-piece, Saddles, Reducers, Flanges and MH Couplings 4.5 - Soc-Sp RRJ 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Sewer Pipe | Use is subject to acceptance by SP
54 | C: Global Pipe; D: Fiberstrong; E: DN300 - DN4000
55 | C: Superlit / Clover Pipelines; D: Superlit; E: DN300 - DN3000
56 | CC-GRP (centrifugally cast) pipe and Fittings - Jacking Pipe | 205J 4.1 - As per product 4.2 - Pressure Class by design 4.3 - Stiffness Class by design 4.4 - Jacking Load by design 4.5 - 316 Stainless Steel (min) or GRP couplings 4.6 - SBR & EPDM 4.7 - Pipe Lengths to manufacturers requirements 4.8 - Standard Glass | Hobas / Global Pipe | Hobas | DN250 - DN3600 | Jacking pipes | Use is subject to acceptance by SP
57 | C: Empire Infrastructure; D: BOSSPIPE; E: DN300 - DN2000
58 | C: Superlit / Clover Pipelines; D: Superlit; E: DN400 - DN1400
59 | FW-GRP (filament wound) pipe and Fittings - Jacking Pipe | 206J 4.1 - As per product 4.2 - Pressure Class by design 4.3 - Stiffness Class by design 4.4 - Jacking Load by design 4.5 - 316 Stainless Steel (min) or GRP couplings 4.6 - SBR & EPDM 4.7 - Pipe Lengths to manufacturers requirements 4.8 - Standard Glass | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Jacking pipes | Use is subject to acceptance by SP
60 | A: Non-return valves; B: No WSA-PS; C: Iplex; D: Flap valve; E: DN50 to DN300; F: All Di fittings to be wrapped
61 | D: Reflux valve fabricated; E: DN100
62 | C: Vinidex; D: Flap valve; E: DN50 to DN100
63 | C: Hygrade Water; D: WaStop Non-return valves; E: DN75 to DN200
64 | C: Fluid Control; D: Red valve - Tideflex check valves; E: DN50 to DN2400
65 | Knife gate valve - Stainless Steel | 266 4.1 - PN10 4.2 - Wafer or Lugged 4.3 - Clockwise closing, rising spindle | Pentair | Keystone | Up to DN600 | Body stainless steel Grade 316. Gate stainless steel Grade 316. Gland Follower stainless steel Grade 304 or 316. Spindle stainless steel grade 304 or 316. Yoke/Pillar/Bridge stainless steel Grade 304 or 316. Seat EPDM, NBR, RTFE or Viton. All fasteners stainless steel Grade 316. | Subject to meeting the corrosion resistance requirements in Column F
66 | C: Challenger; D: Challenger
67 | C: AVFI; D: AVFI
68 | C: HMA Valveco; D: HMA Valveco
69 | C: AVK (Note: This is the only vendor complying with 316 SS throughout); D: AVK
70 | A: Knife gate valve - Fabricated Stainless Steel; B: 266 4.1 - PN1 4.2 - Lugged 4.3 - Clockwise closing, rising spindle (Note: This is a low pressure type gate valve, suitable only for sewer isolation etc.); C: Australian Water Engineers; D: Australian Water Engineers; E: DN700 to DN1200; F: Body, Gate, Gland Follower, Spindle and Yoke / Pillar / Bridge stainless steel Grade 316. Seat EPDM. All fasteners stainless steel Grade 316.
71 | A: Knife gate valve - Ductile iron body; B: 266 4.1 - PN10 4.2 - Wafer or Lugged 4.3 - Clockwise closing, rising spindle; C: Pentair; D: Keystone; E: Up to DN600; F: Body and Gland Follower ductile iron with fusion bonded polymeric coating external to 300 µm, internal to 350 µm (min.) or high-build two-pack epoxy to 275 µm (min.). Gate stainless steel Grade 316. Spindle stainless steel Grade 316. Yoke / Pillar / Bridge carbon steel with fusion bonded polymeric coating to 300 µm or high-build two-pack epoxy to 275 µm (min.). Seat EPDM, NBR, RTFE or Viton. All fasteners stainless steel Grade 316. All DI fittings to be wrapped
72 | C: Challenger; D: Challenger
73 | C: AVFI; D: AVFI
74 | C: AVK; D: AVK
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
75 | A: Category: SEWERAGE PIPES AND FITTINGS - PRESSURE
76 | A: PVC-M pipe; B: 209 4.1 - PN16 4.2 - Sewer Rising main 4.3 - Series 2 only 4.4 - Cream refer POP203 4.5 - SBR & EPDM; AVK C: Iplex; AVK D: BLUERHINO; AVK E: DN100 150 200 225 250 300 & 375; AVK K: NOT ACCEPTED BY SP
77 | AVK C: Vinidex; AVK D: Hydro
78 | AVK C: Viadux; AVK D: TUF-FLO
79 | AVK C: Micron Pipelines; AVK D: Micron Pipelines; AVK E: DN100 - DN300
80 | AVK C: Pipemakers; AVK D: Pipemakers Enviromain
81 | A: PVC-O pipe; B: 210 4.1 - PN16 4.2 - MRS400 or MRS450 4.3 - Sewer Rising main 4.4 - Series 2 only, Cream refer POP203 4.5 - SBR & EPDM; AVK C: Iplex; AVK D: ApolloBLUE; AVK E: DN100 150 200 225 250 300 & 375
82 | AVK C: Vinidex; AVK D: Supermain
83 | AVK C: Micron Pipelines; AVK D: Micron Pipelines; AVK E: DN100 - DN375
84 | AVK C: Pipemakers; AVK D: Alphamain; AVK E: DN100 to DN150; AVK K: Use is subject to acceptance by SP
85 | DI pipe | 200 and WSAA TN6 4.1 - All Pressure Classes - see Column F 4.2 - Seal Coat not required for Sewerage 4.3 - Cement Mortar Linings - see Columns F-K 4.4 - All fittings to be Fusion Bonded Polymeric Coated 4.5 - Restraint Joint Seals by approval 4.6 - SBR and EPDM 4.7 - PE sleeving is required on ALL DI pipes, including those with a zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | Viadux | Tytonxcel | DN250 - 750 (not 225) | PN20 | PN20 NOT ACCEPTED BY SP
86 | AVK C: Vinidex; AVK D: LINX-GP
87 | AVK C: Vinidex; AVK D: ZAP-GP
88 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: PN20, CAC lining for corrosive flows
89 | AVK C: Vinidex; AVK D: LINX-HAC
90 | AVK C: Vinidex; AVK D: ZAP-HAC
91 | AVK C: Viadux; AVK D: Tytonxcel; AVK E: DN100 150 200 250 300 375 450 500 600 & 750 (not 225); AVK F: PN35; AVK K: Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials. Cement mortar lining of any type is not permitted at locations where there is a potential of the pipe lining in contact with air/gas continuously or intermittently. At such locations, non-corrosive pipes or metal pipes with non-corrosive linings shall be used. All linings of pipes and fittings at such locations shall be non-corrosive.
92 | AVK C: Crevet / Iplex; AVK D: Irontite
93 | AVK C: Vinidex; AVK D: LINX-GP
94 | AVK C: Vinidex; AVK D: ZAP-GP
95 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: PN35, CAC lining for corrosive flows
96 | AVK C: Crevet / Iplex; AVK D: Irontite
97 | AVK C: Vinidex; AVK D: LINX-HAC
98 | AVK C: Vinidex; AVK D: ZAP-HAC
99 | AVK C: Viadux; AVK D: Tytonxcel; AVK F: Flange Class
100 | AVK C: Vinidex; AVK D: LINX-GP
101 | AVK C: Vinidex; AVK D: ZAP-GP
102 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: Flange Class, CAC lining for corrosive flows
103 | AVK C: Vinidex; AVK D: LINX-HAC
104 | AVK C: Vinidex; AVK D: ZAP-HAC
105 | AVK C: Saint-Gobain; AVK D: Integral Zinalium; AVK E: DN100 – DN750 (not 225); AVK F: PN35 with CAC lining; Flange Class with CAC lining; AVK K: Use is subject to acceptance by SP
106 | DI Pipe - ISO | 202S 4.1 – K9-PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – Polyurethane lining only 4.4 – Restrained Joints on Zinc/Bitumen coated pipe 4.5 –Only Polyurethane coating on aerial pipes 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | VonRoll / Reece | Ducpur/ Ecopur | DN80 - 700 | Polyurethane internal protection | Use is subject to acceptance by SP
107 | DI fittings - bends, tapers, tees/branches, connectors, risers & caps/blank ends | 201 4.1 - Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by approval 4.4 - SBR & EPDM | Viadux | Tyton Joint | Up to DN750 (not 225) | Thermal bonded polymeric coating is the standard material in WSA PS 201 and WSA PS212 All DI fittings to be wrapped | Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials. Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP.
108 | AVK C: Crevet / Iplex; AVK D: Crevet; AVK E: Up to DN750 (not 225)
109 | AVK C: Vinidex; AVK D: Superlink; AVK E: Up to DN750 (not 225)
110 | AVK C: Derwent; AVK E: Up to DN750 (not 225)
111 | AVK C: Gillies; AVK E: DN100 & DN150
112 | AVK C: Himgiri Castings/Galvin Engineering / CivilPipes; AVK D: Galvin; AVK E: DN80 to DN300
113 | AVK C: Dobbie Dico; AVK D: Dobbie; AVK E: DN100 to DN250
114 | AVK C: Mallet; AVK D: Mallet; AVK E: DN80 to DN750
115 | A: Bolts; B: No WSA-PS Refer Standard Drawing SEQ-WAT-1313-1 etc.; AVK F: 316 Stainless steel bolts; AVK K: Grade 316 Stainless Steel (min.)
116 | A: 316 SS repair and flanged off-take clamps; B: 313 4.1 - Type R or F by SP approval 4.2 - Pipe DN by SP approval 4.3 - Off-take DN by approval 4.4 - Min. PN16; AVK C: Crevet; AVK E: DN100 to DN300; AVK F: Min. PN16, Flanged off-take clamps approved on DI and CI host pipes only, to Pipe manufacturers specifications
117 | AVK C: Viadux; AVK D: Wang; AVK E: DN100 to DN300
118 | AVK C: Cascade Control; AVK D: Rapid Clamps; AVK E: DN40 to DN350
119 | AVK C: Daemco; AVK D: Norma Connect; AVK E: DN80 to DN300
120 | A: Repair Couplings; B: 270 4.1 - PN16 4.2 - All pipe materials 4.3 - Short and Long Series 4.4 - Straight and Stepped 4.5 - All DN Range options 4.6 - Flange end not used 4.7 – EPDM, NBR, Neoprene And SS316 bolts, nuts and washers; AVK C: Nova Siria/Hygrade Water; AVK D: Duofit; AVK E: DN 300 - DN2000; AVK K: Use is subject to acceptance by SP
121 | A: Flange (DI) off-take clamps; B: 327 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation; AVK C: Hawle / Hygrade Water; AVK D: Haku; AVK E: DN125 to DN355; AVK F: For use on PE pipe only, installed and commissioned in accordance with manufacturers recommendations All DI fittings to be wrapped
122 | A: Metal-banded flexible couplings - Vacuum Valve coupling use only; B: 235 4.1 - Need for adaptor bushes where difference between OD of pipe and ID of coupling greater than 16 mm 4.2 - Metal band and bolts shall be min SS316; AVK C: Flex-Seal; AVK D: Flex-Seal; AVK E: Up to DN600; AVK K: NOT ACCEPTED BY SP
123 | AVK C: DEKS; AVK D: DEKS shear banded coupling; AVK E: DN100 to DN225
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
124 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; DEKS C: Viadux; DEKS shear banded coupling D: Gibault - Ezigib & Varigib; DN100 to DN225 F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
125 | DEKS C: Crevet; DEKS shear banded coupling D: Gibault & Universal
126 | DEKS C: AVK; DEKS shear banded coupling D: Gibault & Universal
127 | DEKS C: Viking Johnson; DEKS shear banded coupling D: MaxiFit, QuickFit
128 | DEKS C: Derwent
129 | DEKS C: DEKS; DEKS shear banded coupling D: DEKS FLEXI-GIB; DN100 to DN225 E: DN80 to DN600
130 | DEKS C: Daemco; DEKS shear banded coupling D: Reinoversal; DN100 to DN225 E: Up to DN 600
131 | DI mechanical fittings - End Thrust Restraint (Gripper Type) | 271 for DI, 245 for PE 4.1 - PN16 4.2 - DI and PE 4.3 - Short and Long Series 4.4 - Straight and Stepped and Flange Adaptor 4.5 - All DN Range options 4.6 - Flange Figure as specified with SS316 bolts, nuts and washers 4.7 - SBR & EPDM & Nitrile And SS316 bolts, nuts and washers | DI mechanical fittings - End Thrust Restraint (Gripper Type) | System 2000 for PE Synoflex PN16 Restraint for AC, PVC, DICL, SCL, PE | DN50-DN300 | All DI fittings to be wrapped | Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations The use of gripper type fittings on AC, PVC, DI and SCL pipe is subject to acceptance by SP
132 | DEKS C: AVK; DEKS shear banded coupling D: Supa Plus Restraint for PE
133 | DEKS C: +GF+; DEKS shear banded coupling D: Multi/joint 3000 Plus restraint type for AC, PVC, DI, SCL, PE
134 | DEKS C: Viking Johnson; DEKS shear banded coupling D: Aqaufast and Aquagrip Restraint for PE
135 | DEKS C: Nova Siria/Hygrade Water; DEKS shear banded coupling D: Multigrip; DN100 to DN225 E: DN350-DN1400; DN100 to DN225 K: Use is subject to acceptance by SP
136 | A: DI flanged telescopic flexible fitting; B: No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published; DEKS C: Hawle / Hygrade Water WSA PA 12/09; DEKS shear banded coupling D: Vario; DN100 to DN225 E: DN50 - DN200; DN100 to DN225 F: All DI fittings to be wrapped
137 | A: Dismantling joints for Flange Pipe and Fittings; B: 201 4.1 - Fl-Fl for DJ & Fl/Sp for UniFlange 4.2 - Thrust type and non-thrust type minimum PN16 4.3 - Thrust Restraint by Fitting 4.4 - SBR & EPDM; DEKS C: Viadux; DN100 to DN225 F: Thrust restraint type and non-thrust type are Flanged to AS4087 PN16. SS316 bolts, nuts and washers. Larger sizes of UniFlange shall be assessed for available Fitting PN vs Pipeline Test Head. All DI fittings to be wrapped; DN100 to DN225 K: Uni-flange to be used within pit or aboveground locations only
138 | DEKS C: Viking Johnson
139 | DEKS C: Valveco; DEKS shear banded coupling D: Uni-Flange Adaptor; DN100 to DN225 E: DN50-DN500
140 | DEKS C: Hygrade Water; DEKS shear banded coupling D: Pipemate; DN100 to DN225 E: DN80-DN900
141 | DEKS C: AVFI; DEKS shear banded coupling D: AFD10 Series; DN100 to DN225 E: DN80-DN1200
142 | PE pipe | 207 4.1 - PN16 4.2 - Sewer Rising main 4.3 - Coil pipe permitted up to DN125 with Pipe lengths for larger DN 4.4 - Cream refer POP203 4.5 - PE100 only | Iplex | POLIplex | DN40 50 63 90 125 180 250 315 355 450 560 630 800 | For directional drilling installations, minimum SDR 9 (PN20 PE100) unless specified otherwise and install with SS316 tracer wire. Pipe wall thickness to be designed for installation forces. | PE is preferred pipe material
143 | DEKS C: Vinidex; DEKS shear banded coupling D: Sewertech
144 | DEKS C: DMG; DEKS shear banded coupling D: Hi-Vis
145 | DEKS C: Viadux
146 | DEKS C: Poly Pipe; DEKS shear banded coupling D: SewerFlex
147 | DEKS C: Cromford; DEKS shear banded coupling D: Identipipe
148 | DEKS C: Enviropipes; DEKS shear banded coupling D: Enviropressure
149 | DEKS C: ACP; DEKS shear banded coupling D: ACP; DN100 to DN225 K: Use is subject to acceptance by SP
150 | A: PE pipe - High Stress Crack Resistant (HSCR) Polyethylene Pipe; B: 207, POP016 4.1 - PN16 minimum 4.2 - Sewer Rising main 4.3 - Coil pipe permitted up to DN125 with Pipe lengths for larger DN 4.4 - Cream refer POP203 4.5 - HSCR PE100 only; DEKS C: Iplex; DEKS shear banded coupling D: Millennium HSCR PE; DN100 to DN225 E: DN40 50 63 90 125 180 250 315 355 450 560 630 800; DN100 to DN225 F: For directional drilling and pipe bursting installations, minimum SDR 9 (PN20 HSCR PE100) unless specified otherwise and install with SS316 tracer wires. Pipe wall thickness to be specified as normal PE100 as such "extra" strength should be provided.
151 | A: PE fittings; B: 208 2(a) - AS/NZS4129 or EN1555 or EN12201 or EN13244 is acceptable 4.1 - PN16 4.2 - Electrofusion and butt weld 4.3 - Couplings, Reducers, End Caps, Bends, Tees, Stub Flanges 4.4 - Flanges & SS backing rings to AS/NZS 4087 Fig B5 or B7 4.5 - SBR & EPDM; DEKS C: George Fischer; DN100 to DN225 F: Electrofusion fitting to be long type. Stub flange may only to be used for DN450 and larger sizes.
152 | DEKS C: Friatec / Vinidex; DEKS shear banded coupling D: Frialen; DN100 to DN225 E: DN63XDN32 to DN350XDN90
153 | DEKS C: Plasson
154 | DEKS C: Agru; DEKS shear banded coupling D: AGRU; DN100 to DN225 E: Up to DN630
155 | DEKS C: Fusion Group / FusionPlast; DEKS shear banded coupling D: Fusamatic; DN100 to DN225 E: Up to DN630; DN100 to DN225 K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
156 | DEKS C: NUPIGECO; DEKS shear banded coupling D: Elofit; DN100 to DN225 E: DN20 to DN710
157 | A: Full face PE flanges; B: 208 4.1 - PN16 4.2 - Electrofusion and butt weld 4.3 - Full Face Flange with SS backing ring 4.4 - Flange standard AS/NZS 4087 B5 or B7 4.5 - SBR & EPDM; DEKS C: Plasson; DN100 to DN225 E: DN80/DN100; DN100 to DN225 F: Slotted flanges & backing rings suit both DN80 and DN100 to WSAA 98/50; DN100 to DN225 K: Use of stub flanges is subject to acceptance by SP
158 | DEKS C: Iplex; DN100 to DN225 E: Up to DN355; DN100 to DN225 F: Full bore connections
159 | DEKS C: Friatec / Vinidex; DEKS shear banded coupling D: Frialen; DN100 to DN225 E: Up to DN180; DN100 to DN225 F: Metal insert in the flange, backing rings not required; DN100 to DN225 K: Use is subject to acceptance by SP
160 | B: 216 4.1 - PN16 4.2 - Electrofusion and butt weld; DEKS C: Rodney / Vinidex; DEKS shear banded coupling D: Maxi Stub; DN100 to DN225 E: Up to DN355; DN100 to DN225 F: Full bore connection
161 | Steel pipe | 203 4.1 - MPa 1.6 minimum 4.2 - DN by Design subject to SP approval 4.3 - Seal Coat not required 4.4 - Sintakote minimum for above ground 4.5 - Joint requirements by Design 4.6 - Cathodic Protection by design 4.7 - Standard pressure tests 4.8 - Sintapipe lining 4.9 - SBR & EPDM 4.10 - Sintakote minimum | Steel Mains | Sintapipe | DN324 - 813 | RRJ unless otherwise approved | Use is subject to acceptance by SP
162 | Stainless Steel Pipe | No WSA-PS WSAA Materials Fact Sheet No:2 Selection of Stainless Steels WSAA Materials Fact Sheet No:3 Fabricating Stainless Steels | ASSDA accredited fabricators | N/A | DN100 - DN750 | Min. Grade 316 Min. PN16 Flange to AS4087 Fig B5 | Use is subject to acceptance by SP
163 | A: Resilient seated gate valves, thermal bonded polymeric coating; B: 260 4.1 - PN16 4.2 - All End configurations accepted 4.3 - Integral By-pass on DN450 and larger (Unitywater accepts either integral or constructed by-pass as per job specification) 4.4 - Gear Box on DN600 and larger (Refer Mechanical List) 4.5 - FCRC and NBRC only accept valves with clockwise close; BRC, GRC and SBRC only accept valves with anti-clockwise close 4.6 - No requirement for spindle cap colour 4.7 - Extension Spindle to WSA PS - 262 4.8 - Spindle Cap 4.9 - SBR & EPDM; DEKS C: AVK; DEKS shear banded coupling D: Series 57 (light type only for DN100 & 150) Series 570 Series 36/80 Series 01/71 Series 55; DN100 to DN225 E: Up to DN400 Up to DN400 Up to DN300 Up to DN300 DN450 to 600; DN100 to DN225 F: For PE pipes PE gripper Sluice Valves by Hawle E2 System 2000 or AVK Supa Plus Coupling Series 01/70 or equal Sluice Valves with PE stubs for electrofusion acceptable. Some valves may not need by-pass (check with SEQ SPs). All DI fittings to be wrapped
164 | DEKS C: Hawle; DEKS shear banded coupling D: E2; DN100 to DN225 K: Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
165 | DEKS C: Viadux; DEKS shear banded coupling D: Series 500 Auslite II Auslite III; DN100 to DN225 E: DN200 - DN300 Up to DN 400
166 | DEKS C: Karon / Challenger; DEKS shear banded coupling D: Karon; DN100 to DN225 E: DN80 - DN600
167 | DEKS C: AVFI
168 | DEKS C: Betta; DEKS shear banded coupling D: BETTA; DN100 to DN225 E: DN100 - DN375; DN100 to DN225 K: Use is subject to acceptance by SP
169 | DEKS C: AAP Industries; DEKS shear banded coupling D: Maxiflo/appFLO; DN100 to DN225 E: DN80 to DN300; DN100 to DN225 F: WSAA Appraisal 11/26 Issue 2
170 | DEKS C: Derwent Industries; DEKS shear banded coupling D: Derwent; DN100 to DN225 E: DN80 - DN600; DN100 to DN225 F: WSAA Appraisal 1511
171 | DEKS C: DAEMCO; DN100 to DN225 E: DN80 to DN300; DN100 to DN225 F: WSAA Appraisal 1517 (10/05/16)
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
172 | A: Ball Valves; B: 274 4.1 - PN16 4.2 - Body material: 316 stainless steel 4.3 - by product 4.4 - BSPT thread 4.5 - Clockwise closing; DAEMCO C: Pentair / Viadux; DAEMCO D: Keystone; DN80 to DN300 E: Up to DN50; WSAA Appraisal 1517 (10/05/16) F: BSPT threaded connections Sutiable for sewage
173 | DAEMCO C: AVFI; DAEMCO D: V1 Series - 1 Piece V2 Series - 2 Piece V3 Series - 3 Piece V2FH Series- Flanged; DN80 to DN300 E: DN8 – DN50 DN8 – DN100 DN8 – DN100 DN15 - DN50
174 | CC-GRP (centrifugally cast) pipe and Fittings - Sewer Pipe | 237S 4.1 - PN1 4.2 - SN10,000 minimum 4.3 - Soc-Sp RRJ 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | DI Fittings to WSA PS 201 for Tees and Bends | Use is subject to acceptance by SP Coupling - Grade 316 Stainless Steel (min.)
175 | FW-GRP (filament wound) pipe and Fittings - Sewer Pipe | 205S 4.1 - As per product 4.2 - PN1 4.3 - SN10,000 minimum 4.4 - Bends, T-piece, Y-piece, Saddles, Reducers, Flanges and MH Couplings 4.5 - Soc-Sp RRJ 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | DI Fittings to WSA PS 201 for Tees and Bends | Use is subject to acceptance by SP Coupling - Grade 316 Stainless Steel (min.)
176 | DAEMCO C: Global Pipe; DAEMCO D: Fiberstrong; DN80 to DN300 E: DN300 - DN4000
177 | DAEMCO C: Superlit / Clover Pipelines; DAEMCO D: Superlit; DN80 to DN300 E: DN300 - DN3000
178 | A: Flowmeter - Network Meter; B: No WSAA PS 4.1 - Flange to AS4087 Figure 5 4.2 - PN16; DAEMCO C: ABB; DAEMCO D: ABB; WSAA Appraisal 1517 (10/05/16) K: ABB Water master
179 | DAEMCO C: Siemens; DAEMCO D: Siemens; WSAA Appraisal 1517 (10/05/16) K: Use is subject to acceptance by SP
180 | DAEMCO C: E & H; DAEMCO D: E & H; WSAA Appraisal 1517 (10/05/16) K: Use is subject to acceptance by SP
181 | DAEMCO C: Emerson; DAEMCO D: Emerson
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
182 | A: Category: SEWERAGE MISCELLANEOUS ITEMS
183 | A: Maintenance structure covers, frames and risers; B: 290 4.1 - DN600 4.2 - Round Solid Top ( Conc Infill - QUU only ) Sealed Type 4.3 - 600 mm Clear Opening 4.4 - Class B and Class D 4.5 - Rocking of cover in frame not permitted 4.6 - Lifting Key as per Standard Drawings 4.7 - Markings to AS3996 Clause 1.6 (a) to (f). 4.8 - No Hinge 4.9 - Standard Packaging and Delivery 4.10 - QUU require QUU cast in as per Standard Drawings 4.11 - Standard Coating 4.12 - Bolt down for Surcharge and overland flow areas, 4 x M8 (min) SS316 Bolts 4.13 - by Standards; Emerson C: Gatic / Milne; Emerson F: Refer Standard Drawings. Covers with another Service Provider's name not accepted. Use of Square and Rectangular Covers and Frames subject to SP approved based on Design needs; Emerson K: Concrete Infill Covers NOT ACCEPTED BY SP
184 | Emerson C: East Jordan (Havestock)
185 | Emerson C: Webforge
186 | Emerson C: Tellam
187 | Emerson C: Durham
188 | Emerson C: Hygrade
189 | A: Maintenance shaft covers, frames and risers DN<=450; B: 292 4.1-DN<=450 Round 4.2-DN360 min clear opening 4.3-Standard Lifting Key 4.4-Markings to AS3996 Clause 1.6 (a) to (f) 4.5-Standard packaging 4.6-No specific markings required 4.7-No bolt down required; Emerson C: Smartstream; Emerson D: Smartstream Top Hat- P8HDS; Emerson F: DI-Class D
190 | Emerson C: Smartstream; Emerson D: Smartstream Top Hat- P8PEC; Emerson F: PE - Class B
191 | Emerson C: SYI Foundry/Aymroo; Emerson D: Aymroo; Emerson E: 360 mm clear opening; Emerson F: CI - Class B
192 | A: Maintenance hole lightweight composite lids and frames (non- corrosive); B: 292 4.1-DN>=600 Round 4.2-DN600 min clear opening 4.3-Standard Lifting Key 4.4-Markings to AS3996 Clause 1.6 (a) to (f) 4.5-Standard packaging 4.6-No specific markings required 4.7-Bolt down for Surcharge and overland flow areas, 2 x M8 min SS316 Bolts; Emerson C: Terra Firma; Emerson F: Composite - Class B and D; Emerson K: Use is subject to acceptance by SP
193 | Emerson C: ACO SAKU; Emerson F: Composite - Class B
194 | Emerson C: Prime Composites; Emerson F: Composite – Class B and D; Emerson K: Use is subject to acceptance by SP
195 | A: Emergency Storage maintenance hole cover; B: 290 4.1 – DN1000 4.2 – Two part round 4.3 – 920 mm Clear Opening 4.4 – Class C 4.5 – Rocking of cover in frame not permitted 4.6 – Hand grip lifting points 4.7 – No requirements 4.8 – Central Hinge not required 4.9 – Standard Packaging and Delivery 4.10 – No requirements 4.11 – No requirements 4.12 – 4 x 3/8” Allen Key SS 316 Bolts 4.13 – Nil Seat ring SS 316; Emerson C: Treloar; Emerson D: MC1000-Manway Cover; Emerson E: DN900; Emerson F: Class C Fabricated S/Steel grade 316 ring Nitrile gasket seal
196 | A: Step irons; B: 314 4.1 - Single Step 4.2 - Complies with Figure 5.10 of AS1657 4.3 - Steel bar internal with Plastic encapsulation or SS316 4.4 - Plastic encapsulation or SS316 4.5 - No reflectors required 4.6 - No other safety devices required; Emerson C: Miyama / Nextep; Emerson D: Miyama; Emerson F: M053; Emerson K: NOT ACCEPTED BY SP
197 | Emerson C: Aymroo; Emerson D: Aymroo
198 | Emerson C: C & C Plastics / Havestock; Emerson D: Posistep
199 | Emerson C: Industrial Steps & Ladders; Emerson D: Sure-Step
200 | A: Ladders; B: 315 4.1 - Type D - Fixed Ladder with two Stiles 4.2 - PBT, FRP, SS316, Galvanised Steel or Aluminium 4.3 - By Standards 4.4 - By Standards 4.5 - Reflectors optional 4.6 - 150 mm from CL of rung to MH wall 4.7 - By Standards 4.8 - Colour as per material 4.9 - SS 316; Emerson C: Miyama / Nextep; Emerson D: Miyama; Emerson F: Fibre reinforced plastics (yellow). Brackets & Fasteners to be SS316 Min. Clearances for Rung Type Ladders as per AS1657 Fixed Platforms, Walkways, Stairways and Ladders - Design and Installation; Emerson K: NOT ACCEPTED BY SP
201 | Emerson C: Industrial Steps & Ladders; Emerson D: Add-A-Step; Emerson F: Revised installation procedure WSAA Product Update 1- 2011, Subject to WSAA appraisal 5/11 and WSAA Product Alert 1-2010. Brackets as per manufacture specification. Fasteners to be SS316. Bright yellow.
202 | Emerson C: Galvanised Steel; Emerson F: Refer to Standard Drawings
203 | Emerson C: Stainless Steel or Aluminium
204 | Maintenance Shaft PVC | 321 4.1 - As per Standards 4.2 - As per Specifications 4.3 - As per Standards 4.4 - Inlet and Outlet at DN150 to DN225 4.5 - Configurations as shown in Standard drawings 4.6 - As per accepted product 4.7 - Inlet and Outlet Sewer connection RRJ 4.8 - Cap as shown in Standard Drawings 4.9 - As per Standard Drawings 4.10 - Connect to PCV-U DWV pipe 4.11 - Max depth 3.0 metres FSL to Invert of Sewer Pipe | Aymroo | Aymroo | DN225 PVC-U Riser Shaft | Configurations of "Central Axis" maintenance shaft (CAMS) are not accepted | DN225 risers not accepted. Min DN300 risers are accepted.
205 | Emerson C: SMS; Emerson D: SMS # MS3 DN150 Only
206 | A: Maintenance Shafts PE; B: 322 4.1 - As per Standards 4.2 - As per Specifications 4.3 - As per Standards 4.4.a - Inlet and Outlet at DN150 to DN225 for PVC RIGSS 4.4.b - Inlet and Outlet at DN160 to DN250 for PE Nusewer 4.5 - Configurations as shown in Standard drawings 4.6 - As per accepted product 4.7.a - Inlet and Outlet PVC Sewer connection RRJ 4.7.b - Inlet and Outlet PE Sewer connection Electrofusion 4.8 - Cap as shown in Standard Drawings 4.9 - As per Standard Drawings 4.10 - Max depth 3.0 metres FSL to Invert of Pipe; Emerson C: Smartstream; Emerson D: Poo-Pit; Emerson F: RIGSS DN225 PVC riser shaft. Nusewer fully welded with DN250 PE risers and sewer stubs.; Emerson K: DN225 risers not accepted. Min DN300 risers are accepted.
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
207 | A: Maintenance Shafts Polypropylene - DN425 and DN600 risers; B: 337, 341 4.1 – DN425 and DN600 Risers 4.2 – Polypropylene Riser 4.3 – DN425 SN4 & DN600 SN8 riser pipe 4.4A – DN425 Base with DN150 sewer 4.4B – DN600 Base with DN150/225 sewer 4.5 – In-line and bends and tees 4.6 – Base and Riser ribbed 4.7A – EPDM or SBR Ring Joints RIGSS 4.8 – No locking or relief cap 4.9 - Standard MH surround, cover and frame 4.10- Max depth 3.0 meters to Invert of Sewer Pipe; C: Iplex; D: EZIpit PA 09/01 & PA 09/1-2; F: Refer Standard Drawings; K: Approved for DN150 to DN225 RIGSS only as per cell B, Base is single DN size, NOT ACCEPTED FOR NUSEWER
208 | A: Maintenance Shafts Polypropylene - DN225 and DN300 risers; B: 341 4.1 – DN225 and DN300 Risers 4.2 – PVC Riser 4.3 – SN8 riser pipe 4.4 - DN150 sewer 4.5 – In-line and bends and tees 4.6 – Base ribbed, Riser Solid Wall PVC 4.7 – EPDM or SBR Ring Joints RIGSS 4.8 –Locking relief cap as per Standard Drawings 4.9 - Standard MH surround, cover and frame 4.10- Max depth 3.0 meters to Invert of Sewer Pipe; C: SMS; D: SMS PA 09/08 parts 0 to 5 Code: MS1 Code: MS2 Code: MS5; F: Refer Standard Drawings; K: Approved for DN150 RIGSS only. DN225 risers not accepted. Min DN300 risers are accepted.
209 | C: REHAU; D: OD400-GD (Type H12) OD400-RML (Type H13)
210 | A: Pre-cast Maintenance Holes; B: 323 4.1a - DN1000 minimum MH 4.1b - DN600 minimum MS 4.2 - Configurations as per Standard Drawings 4.3 - No step irons or ladders 4.4 - Elastomeric and Butyl rubber seals accepted 4.5 - Calcareous aggregates no additional cover 4.6 - No special treatments 4.7 - Base format as per SEQ SP approval 4.8 - Configurations as per Standard Drawings; C: Humes; E: MH and MS DN150 and DN225 sewers; F: Refer Standard Drawings Use for larger Sewer DN's and MH diameters is subject to acceptance by SP Max depth of DN600 MS FSL to Invert of Pipe is 3.0 meters; K: Pre-cast MHs accepted Use of MS is subject to acceptance by SP
211 | C: Rocla
212 | A: Pre-cast Concrete Converter Slab for Cast In-situ MHs; B: No WSA-PS Refer Standard Drawings; C: Everhard; F: Refer Standard Drawings Calcareous aggregates to be used
213 | C: Tellam
214 | A: Plastic Maintenance Holes; B: No WSA-PS Refer details of Type K1 on SEQ-SEW-1314-2 Minimum DN1000 chamber and DN600 neck; C: Smartstream; D: Smart Pit; E: DN150 to DN300 sewers; F: Refer Standard drawings Max depth FSL to Invert of Pipe is 3.0 meters
215 | A: Vent poles; B: 325 Project Specific outcome Product Appraisal Report PA 0906 for RPC; C: RPC Technologies; F: Refer Standard Drawings Tapered, Galvanised, height as design preferred colour: heritage or mist green; K: Use is subject to acceptance by SP
216 | C: Ingal EPS; K: Minimum accepted Height 6.0 m
217 | A: Valve box and cover C.I. & D.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1305-2; C: Viadux; F: Refer Water Code Standard Drawings for approved Valve Box and Cover
218 | C: NIBF
219 | C: Gatic / Milne
220 | C: Tellam
221 | A: Loose PE sleeving to DI pipe; B: 320 Cream Colour to POP203; C: Viadux; D: BLUEBOSS Cream; F: Mandatory sleeving to all DI pipe
222 | C: Crevet
223 | A: Embedment material - crushed rock; B: 351 4.1 - Single sized 4.2 - Nominal 5 or 7 mm
224 | A: Embedment material - recycled concrete; B: 366 4.1 - Single sized 10 mm nominal 4.2 - Moisture Content by design; C: Queensland Recycling; K: NOT ACCEPTED BY SP
225 | A: Concrete-Normal Class; B: 357 4.1 - As follows N20 Thrust Blocks N25 for reinforced embedment 4.2 - Slump as required for placement
226 | A: Concrete-Special Class (for Maintenance hole and for concrete in aggressive environment); B: 358 4.1 - SCC40 with Fly Ash/Type SR Portland Cement ratio of 0.25 to 0.30. 4.2 - Slump as required for placement 4.3 - Calcareous aggregate at 20 mm; K: Calcareous aggregate size to be 10mm minimum. Admixtures shall be non-chloride type
227 | A: Gas release valves; B: 275 Refer Appendix B of AS4883 Size of Valve - DN50 BSP, DN50 to DN200 Flanged. Class of valve - PN16 Type of Port - Full and Reduced port Type of Valve - As per design needs Hydraulic Data - By design to AS4883 Appendix B; C: ARI Flow control; E: DN50-DN200; F: PN16, Anti Slam as required, Thermal bonded polymeric coating or 316 Stainless steel
228 | C: Bermad
229 | C: Vent-O-Mat
230 | C: Odour Technologies; D: Vinloc-Smartvalve
231 | C: AVFI; D: ARV-3-N
232 | C: ISCO; D: Vent Master PX
233 | Non-return valves - Swing check with counterweight lever arm | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Sewage c) Installation - Horizontal d) Spindle - Extended e) Lever and Counterweight minimum with switches and indicators by Design j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | MIN. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP
234 | C: Dobbie Dico; D: Dobbie Dico; E: DN80-DN900
235 | C: AVK; D: AVK Swing Check Valve 41/25; E: DN50
236 | C: AVK; D: AVK Swing Check Valve 41/8X; E: DN80-DN300
237 | C: Challenger Valves; D: Challenger - RSSC; E: DN80-DN375
238 | C: AVFI Pty Ltd; D: AVFI - RSFC; E: DN50-DN300
239 | A: Non-return valves - free acting (without counterweight) Swing Check; B: 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Sewage c) Installation - Horizontal d) Spindle - Extended j) Flanged to AS 4087 Figure B5; C: HMA Valveco; D: Valmatic Swing-flex; E: DN50 - DN600; F: MIN. PN16, Thermal bonded polymeric coating
240 | C: Dobbie Dico; D: Dobbie Dico; E: DN80-DN900; K: Use is subject to acceptance by SP
241 | C: AVK; D: AVK Swing Check Valve 41/25; E: DN50
242 | C: AVK; D: AVK Swing Check Valve 41/8X; E: DN80-DN300
243 | C: Challenger Valves; D: Challenger - RSSC; E: DN80-DN375
244 | C: AVFI Pty Ltd; D: AVFI - RSFC; E: DN50-DN300
245 | PVC-U Fabricated Fittings Fibreglass reinforced PVC Type 'D' junctions & fittings | 230 4.1 - Plain Wall only 4.2 - Solvent Cement joints for Fabricated assemblies with Elastomeric Seal on Fitting Socket Ends 4.3 - Pipe DN100 @ SN6 min and Pipe DN150 and larger SN8 min. Fittings SN6 min 4.4 - RRJ @ SBR & EPDM | Vinidex | Deep Sewer Junction & Reinforced Fittings such as Oblique Junctions and House Connection Bends and Inspection Tees | DN100-300 | DWV uPVC Moulded Fitting reinforced to SEQ Standards. Type D Junction from moulded fittings welded and fibreglass wrapped. 45 Deg Oblique Jn and Property Connection bends and Inspection Tees fibreglass wrapped. Fabricator has Certification to Section 6 of AS/NZS 1260 and fittings Fibreglass wrapped as shown on the drawings SEQ-SEW-1104-1 and SEQ-SEW-1105-1. | DN100 at SN10, DN150 and larger at SN8 and Fittings at SN8 minimum
246 | C: Iplex
247 | C: Fabfit
248 | C: M.E. Christensen
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
249 | A: PVC-U SN8 long radius bends; B: 236 4.1 - SN8 minimum 4.2.1 - DN150 only, 3.0 metres radius as a heat formed bend with standard socket and spigot RRJ ends. No ovality variation permitted. 4.2.2 - DN225 only, 3.0 metres radius preferred, spigot spigot ends as a heat formed bend or as a fibreglass wrapped fabricated bend with 7.5 degree segments with 300 mm to 400 mm segment length on inside springline 4.2.3 - All long radius bends by Certified fabricators to AS/NZS 1260 Section 6 4.3 - SBR & EPDM; M.E. Christensen C: Vinidex; M.E. Christensen D: Long radius 3000 mm bends; M.E. Christensen E: DN150 as bent pipe & DN225 as bent or fabricated pipe; M.E. Christensen F: AS/NZS 1260 SN8 DN150 Bends available from 5Deg to 45Deg. DN225 and larger individually fabricated to 45Deg.
250 | M.E. Christensen C: Iplex
251 | M.E. Christensen C: Tri Underground
252 | M.E. Christensen C: Fabfit
253 | M.E. Christensen C: M.E. Christensen
254 | A: Detectable marker tape; B: 318 4.1 - Tape/Product Colour - Drinking Water = Blue Non-Drinking Water = Purple. Sewerage = Cream 4.2 - Message = "Caution ASSET DESCRIPTION Buried Below" or "Danger Buried ASSET DESCRIPTION Below" 4.3 - SS 316 tracer wire 4.4 - See 4.1 above; M.E. Christensen C: Boddingtons
255 | M.E. Christensen C: Tapex
256 | M.E. Christensen C: Rain Harvesting; M.E. Christensen D: 421
257 | A: Tracer wire; B: 343 4.1 - CCS shall be AISI 1055 grade or higher 4.2 - Wire gauge Shall be 12 or thicker 4.3 - Minimum 520Kg 4.4 - Minimum 45mil 4.5 - minimum 1% 4.6 - as per standards 4.7 - as per standards 4.8 - Blue for Water Supply, Purple for Recycled Water and Cream for Pressure Sewer.; M.E. Christensen C: Tapex; M.E. Christensen D: Copperhead; M.E. Christensen E: 500, 1000 and 2500 (feet); M.E. Christensen F: Approved are SoloShot EHS and SoloShot Xtreme For HDD and Pipe bursting etc. Components of test station, connector and grounding anode are accepted
258 | A: Security fencing; M.E. Christensen F: AS1725.1 Chain Link Fabric Fencing-powder coated black
259 | A: Hydrophilic Seal; M.E. Christensen D: Hydrotite
260 | A: Casing Spacers; B: 324 4.1 - Carrier pipes OD from 100mm to 1668mm 4.2 - Min space between carrier pipes and encasing pipes 50mm; M.E. Christensen C: kwik-ZIP; M.E. Christensen D: kwik-ZIP; M.E. Christensen E: HDX Series with Runner height of 38, 65, 90 and 125 mm; M.E. Christensen F: For SCL, DI, PE, PVC, Concrete, GRP and FRP carrier pipes
261 | Protective lining & coating (including PE lining) | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list
262 | A: Camlock; M.E. Christensen F: S/Steel 316; M.E. Christensen K: Maximum DN100
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
263 | Camlock A: Category: WATER SUPPLY PIPES - PRESSURE
264 | Camlock A: PVC-M pipe; Camlock B: 209 4.1 - PN16 4.2 - Drinking Water 4.3 - Series 2 only 4.4 - Blue 4.5 - SBR & EPDM; Camlock C: Iplex; Camlock D: Reiber Blue; S/Steel 316 F: Series 2 PN16, Min SN 10 Reiber ring accepted; Maximum DN100 K: NOT ACCEPTED BY SP
265 | Camlock C: Vinidex; Camlock D: Hydro Blue; Camlock E: DN100 to DN300
266 | Camlock C: Viadux; Camlock D: Tuf-Flo
267 | Camlock C: Micron Pipelines; Camlock D: Micron Pipelines; Camlock E: DN100 to DN300
268 | Camlock C: Pipemakers; Camlock D: Pipemakers Enviromain
269 | Camlock A: PVC-O pipe; Camlock B: 210 4.1 - PN16 4.2 - MRS400 or MRS450 4.3 - Water main 4.4 - Series 2 only, Blue for Drinking Water and Purple for No- Drinking Water refer POP203 4.5 - SBR & EPDM; Camlock C: Iplex; Camlock D: Apollo Blue; Camlock E: DN100 to DN300; S/Steel 316 F: Series 2 PN16, Min SN 10 MRS400 or MRS450
270 | Camlock C: Vinidex; Camlock D: Supermain
271 | Camlock C: Micron Pipelines; Camlock D: Micron Pipelines; Camlock E: DN100 - DN375
272 | Camlock C: Pipemakers; Camlock D: Alphamain; Camlock E: DN100 to DN150
273 | DICL pipe | 200 4.1 - All Pressure Classes - see Column F 4.2 - As per Standards 4.3 - As per accepted product 4.4 - All fittings to be Fusion Bonded Polymeric Coated 4.5 - Restraint Joint Seals by approval 4.6 - SBR and EPDM 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | Viadux | Tytonxcel | DN250 - 750 (not 225) | PN 20 | Seal coat on pipes >= 450 Seal coat requirement is dependant on water quality. PN20 - Use is subject to acceptance by SP Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials.
274 | Camlock C: Vinidex; Camlock D: LINX-GP
275 | Camlock C: Vinidex; Camlock D: ZAP-GP
276 | Camlock C: Viadux; Camlock D: Tytonexcel; Camlock E: Up to DN750 (not 225); S/Steel 316 F: PN 35
277 | Camlock C: Crevet / Iplex; Camlock D: Irontite
278 | Camlock C: Vinidex; Camlock D: LINX-GP
279 | Camlock C: Vinidex; Camlock D: ZAP-GP
280 | Camlock C: Viadux; Camlock D: Flange Class; S/Steel 316 F: Flange Class
281 | Camlock C: Vinidex; Camlock D: LINX-GP
282 | Camlock C: Vinidex; Camlock D: ZAP-GP
283 | Camlock C: Saint-Gobain; Camlock D: Hydroclass Zinalium; Camlock E: DN100 – DN750 (not 225); S/Steel 316 F: PN35, Flange Class; Maximum DN100 K: Use is subject to acceptance by SP
284 | DI Pipe - ISO | 202 4.1 – K9-PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 –Restrained Joints on Zinc/Bitumen coated pipe 4.4 –Polyurethane without seal coating 4.5 - Only Polyurethane coating on aerial pipes 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | VonRoll / Reece | Ducpur/ Ecopur | DN80 - 700 | Polyurethane internal protection | Use is subject to acceptance by SP
285 | Camlock A: Small DN Ductile Iron Water Main pipe at PE OD’s; Camlock C: Saint-Gobain PAM; Camlock D: BLUTOP; Camlock E: DN75-DN160; S/Steel 316 F: Restrained Joints PN16 Unrestrained joints PN25; Maximum DN100 K: Use is subject to acceptance by SP
286 | SCL pipe | 203 4.1 - MPa 1.6 minimum 4.2 - DN by Design subject to SP approval 4.3 - Seal Coat required for DN450 and larger 4.4 - Sintakote minimum for above ground 4.5 - Joint requirements by Design 4.6 - Cathodic Protection by design 4.7 - Standard pressure tests 4.8 - Sintapipe lining option 4.9 - SBR & EPDM 4.10 - Sintakote minimum | Steel Mains | Sintakote | OD114, 168, 219, 257, 273, 324 to 2159. | Minimum thickness DN100 - 4.8 mm, >DN100 - 5 mm | Seal Coat requirement is dependant on water quality
287 | Camlock A: PE pipe; Camlock B: 207 4.1 - PN16 SDR11 PE100 4.2 - Drinking and Non-Drinking Water 4.3 - Pipes lengths for DN160 and larger and coils accepted for DN110 and smaller 4.4 - Mains Colour Blue Solid for Drinking Water and Purple solid for Non-Drinking Water with Water Service pipe Black with Blue Stripes for Drinking Water and Purple solid for Non-Drinking Water, refer POP203. 4.5 - PE100 only; Camlock C: Iplex; Camlock E: OD25 32 40 50 63 90 125 180 250 315 355 450 560 630 800; S/Steel 316 F: PE100 PN16 Blue colour - solid or striped for drinking water Purple colour - solid for non-drinking water For directional drilling installations, minimum SDR 9 (PN20 PE100) unless specified otherwise and install with SS316 tracer wire. Pipe wall thickness to be designed for installation forces.
288 | Camlock C: Vinidex
289 | Camlock C: DMG
290 | Camlock C: Cromford; Camlock D: Identi-pipe
291 | Camlock C: Poly Pipe
292 | Camlock C: Viadux; Camlock D: Advantage/TYCO10
293 | Camlock C: Enviropipes; Camlock D: Enviropressure
294 | Camlock C: ACP; Camlock D: ACP; Maximum DN100 K: Use is subject to acceptance by SP
295 | Camlock A: PE pipe - High Stress Crack Resistant (HSCR) Polyethylene Pipe; Camlock B: 207, POP016 4.1 - PN16 minimum 4.2 - Drinking and Non-Drinking Water 4.3 - Pipes lengths for DN160 and larger and coils accepted for DN110 and smaller 4.4 - Mains Colour Blue Solid for Drinking Water and Purple solid for Non-Drinking Water with Water Service pipe Black with Blue Stripes for Drinking Water and Purple solid for Non-Drinking Water, refer POP203. 4.5 - HSCR PE100 only; Camlock C: Iplex; Camlock D: Millennium HSCR PE; Camlock E: DN25 32 40 50 63 90 125 180 250 315 355 450 560 630 800; S/Steel 316 F: For directional drilling and pipe bursting installations, minimum SDR 9 (PN20 HSCR PE100) unless specified otherwise and install with SS316 tracer wires. Pipe wall thickness to be specified as normal PE100 as such "extra" strength should be provided.
296 | Camlock A: Copper pipe; Camlock B: 214 4.1 - Annealed for all pipe 4.2 - Natural pipe colour; Camlock C: Port Kembla Copper; Maximum DN100 K: Use is subject to acceptance by SP
297 | CC-GRP (centrifugally cast) pipe and Fittings - Water main | 237 4.1 - PN16 minimum 4.2 - SN 10,000 minimum 4.3 - Sp-Sp RRJ Coupling and Fl Joints 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | Minimum SN10000, PN16 | Use is subject to acceptance by SP
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
298 | FW-GRP (filament wound) pipe and Fittings - Water main | 205 4.1 - DN300 and larger 4.2 - PN16 minimum 4.3 - SN 10,000 minimum 4.4 - Standard bend forms permitted 4.5 - Sp-Sp RRJ Coupling and Fl Joints 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Minimum SN10000, PN16 | Use is subject to acceptance by SP
299 | C: Global Pipe; D: Fiberstrong; E: DN300 - DN4000
300 | C: Superlit / Clover Pipelines; D: Superlit; E: DN300 - DN3000
301 | Stainless Steel Pipe | No WSA-SP WSAA Materials Fact Sheet No:2 Selection of Stainless Steels WSAA Materials Fact Sheet No:3 Fabricating Stainless Steels | ASSDA accredited fabricators | N/A | DN100 - DN750 | Min. Grade 316 Min. PN16 Flange to AS4087 Fig B5 | Use is subject to acceptance by SP
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
302 | A: Category: WATER SUPPLY FITTINGS - PRESSURE
303 | Lightweight DI bends, tees/branches & connectors | 201 4.1 - Soc-Soc, Soc-Fl & Fl-Fl 4.2 - PN16 fittings 4.3 - By approval 4.3 - SBR & EPDM | Viadux | Auslite | DN100 & DN150 | Lightweight fittings Thermal bonded polymeric coating All DI fittings to be wrapped | Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP
304 | C: Dobbie Dico; D: Dobbie; E: DN100 to DN150
305 | C: Himigiri Castings/Galvin Engineering / CivilPipes; D: Galvin; E: DN100 & DN150; K: Use is subject to acceptance by SP
306 | DI bends, tapers, tees/branches, connectors, risers & caps/blank ends | 201 4.1 - Soc-Soc, Sp-Sp, Fl-Fl, Soc-Sp, Soc-Fl & Sp-Fl 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by SP approval 4.4 - SBR & EPDM | Viadux | Tyton Joint | Up to DN750 | Thermal bonded polymeric coating All DI fittings to be wrapped | Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP
307 | C: Crevet / Iplex; D: Crevet
308 | C: Vinidex; D: Superlink
309 | C: Derwent
310 | C: Gillies; E: DN100 & DN150
311 | C: Himigiri Castings/Galvin Engineering / CivilPipes; D: Galvin; E: DN80 to DN300
312 | C: Dobbie Dico; D: Dobbie; E: DN100 to DN250
313 | C: Mallet; D: Mallet; E: DN80 to DN750
314 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; C: Viadux; D: Gibault Ezigib & Vari-Gib; F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
315 | C: Crevet; D: Gibault & Universal Multigib; E: Up to DN750
316 | C: AVK; D: Gibault & Universal
317 | C: Viking Johnson; D: MaxiFit, QuickFit
318 | C: Derwent
319 | C: DEKS; D: DEKS FLEXI-GIB; E: DN80 to DN750
320 | C: Daemco; D: Reinoversal; E: Up to DN 600
321 | A: DI mechanical couplings - End Thrust Restraint (Gripper Type); B: 271 4.1 - PN16 4.2 - DI 4.3 - Short and Long Series 4.4 - Straight and Stepped and Flange Adaptor 4.5 - All DN Range options 4.6 - Flange Figure as specified with SS316 bolts, nuts and washers 4.7 - SBR & EPDM & Nitrile And SS316 bolts, nuts and washers; C: Hawle / Hygrade Water; D: Synoflex PN16 Restraint coupling for AC, PVC, DICL, SCL; E: DN50-DN300; K: The use of gripper type fittings on AC, PVC, DI and SCL pipe subject to acceptance by SP
322 | C: +GF+; D: Multi/ joint 3000 Plus restraint type for AC, PVC, DICL, SCL
323 | C: Nova Siria/Hygrade Water; D: Multigrip for all pipe material, For PVC and PE pipes use Nova Siria reinforcing liner inside the pipe when installing multigrip; E: DN350-DN1400; K: Use is subject to acceptance by SP
324 | A: DI flanged telescopic flexible fitting; B: No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published; C: Hawle / Hygrade Water; D: Vario WSA PA 12/09; E: DN50 - DN200
325 | A: Small DN Ductile Iron Restraint Fittings at PE ODs; C: Saint-Gobain PAM; D: IZIFIT; E: DN75-DN160; F: For use directly with PE and BLUTOP pipe.; K: Use is subject to acceptance by SP
326 | A: Pretapped connectors; B: 201 4.1 - Soc-Soc only 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by approval 4.4 - SBR & EPDM DN100 to DN150 with 4 x 20BSP tappings at 2 per side and DN200 to DN300 1 x 50BSP tapping; C: Viadux; D: Readytap; E: DN100 to 300; F: Thermal bonded polymeric coating DN100 to DN150 with 4 x 20BSP tappings at 2 per side and DN200 to DN300 1 x 50BSP tapping
327 | C: Crevet / Iplex; D: Pretapped; E: DN100 & DN150
328 | C: Vinidex; D: Superlink; E: DN100 & DN150
329 | C: Himigiri Castings/Galvin Engineering / CivilPipes; D: Galvin; E: DN100 & DN150; K: Use is subject to acceptance by SP
330 | B: 246 4.1 – Blue or Black for DW and Purple for NDW; C: 4N Products & Stockbrands; D: Supertap; E: DN100 & 150; F: Only used on Series 2 PVC pipe Not suitable for DI pipe WSAA Appraisal 12/18
331 | A: 316 SS repair clamps, flanged off- take clamps & BSP tapping clamps; B: 313 4.1 - Type R or F by SP approval 4.2 - Pipe DN by SP approval 4.3 - Off-take DN by approval 4.4 - Min. PN16; C: Crevet; D: Wang; E: DN100 to DN300; F: Min. PN16, Flanged off-take clamps approved on DI and CI host pipes only, to Pipe manufacturers specifications
332 | C: Viadux; D: Wang; E: DN100 to DN300
333 | C: Cascade Control; D: Rapid Clamps; E: DN40 to DN350
334 | C: Daemco; D: Norma Connect; E: DN80 to DN300
335 | A: Repair Couplings; B: 270 4.1 - PN16 4.2 - All pipe materials 4.3 - Short and Long Series 4.4 - Straight and Stepped 4.5 - All DN Range options 4.6 - Flange end not used 4.7 – EPDM, NBR, Neoprene And SS316 bolts, nuts and washers; C: Nova Siria/Hygrade Water; D: Duofit; E: DN 300 - DN2000; K: Use is subject to acceptance by SP
336 | A: Flange DI off-take clamps; B: 327 4.1 - Pipe DN63 and larger (see WSA PS 207 above) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation; C: Hawle/Hygrade Water; D: Haku; E: DN110 to DN355; F: For use on PE pipe only, installed and commissioned in accordance with manufacturers recommendations
337 | A: Resilient Seated Gate Valves, thermal bonded polymeric coating.; B: 260 4.1 - PN16 4.2 - All End configurations accepted 4.3 - Integral By-pass on DN450 and larger (Unitywater accepts either integral or constructed by-pass as per job specification) 4.4 - Gear Box on DN600 and larger (refer mechanical list) 4.5 - Clockwise for opening 4.6 - No requirement for spindle cap colour 4.7 - Extension Spindle to WSA PS - 262 4.8 - Spindle Cap 4.9 - SBR & EPDM; C: AVK; D: Series 57 (light type only for DN100 & 150) Series 570 Series 36/80 Series 01/71 Series 55; E: Up to DN400 Up to DN400 Up to DN300 Up to DN300 DN450 to 600; F: Anchor legs approved PE Pipe ended approved Gripper ends approved
338 | C: Hawle / Hygrade Water; D: E2 FL Ends E2 System 2000 A Valve FL & SOC Ends; E: DN50 - 200 DN50 - 300 DN80 - 200; F: WSAA Appraisal 11/23 WSAA Appraisal 06/07; K: Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
339 | C: Viadux; D: Series 500 Auslite Auslite II Bayard Sureflow Auslite III; E: Up to DN600 DN80, 100 & 150 DN100 to DN300 DN50 - DN200 Up to DN 400; F: Anchor Legs approved With PE pipe tails approved
340 | C: Karon / Challenger; D: Karon; E: DN80 - DN600
341 | C: AVFI
342 | C: Betta; D: BETTA; E: DN100 - DN375; K: Use is subject to acceptance by SP
343 | C: AAP Industries; D: Maxiflo/appFLO; E: DN80 to DN300; F: WSAA Appraisal 11/26 Issue 2
344 | C: Derwent Industries; D: Derwent; E: DN80 - DN600; F: WSAA Appraisal 1511
345 | C: DAEMCO; E: DN80 to DN300; F: WSAA Appraisal 1517 (10/05/16)
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
346 | Butterfly Valves | 263 4.1- PN16 4.2- resilient seated wafer, lugged or double flanged | Pentair / Viadux | Keystone | DN50-600 for wafer/ lugged DN100-1000 double flanged | Body ductile iron with fusion bonded polymeric coating external to 300 µm, internal to 350 µm (min.) or high- build two-pack epoxy to 500 µm (min.). Disc stainless steel Grade 316. Shaft stainless steel Grade 316, 410, 420, 430 or 431. Seat EPDM. All fasteners stainless steel Grade 316. Operation Type: Lever or Gearbox. Gearbox ratio as per manufacturer’s requirement, coating – high build two-pack Epoxy 275 µm (min.) | Direction of closing: Clockwise Wafer or Lugged valves not accepted without prior approval
347 | DAEMCO C: Ebro; DAEMCO D: Ebro
348 | DAEMCO C: AVFI; DAEMCO D: AVFI
349 | DAEMCO C: Valveco; DAEMCO D: Valveco
350 | DAEMCO C: Iplex; DAEMCO D: AVK
351 | DAEMCO C: Challenger; DAEMCO D: Challenger; WSAA Appraisal 1517 (10/05/16) K: Use is subject to acceptance by SP
352 | DAEMCO C: Hydroflow Distributors; DAEMCO D: Watts
353 | A: Hydrants; B: 267 4.1 - DN80 and DN100 Flanges; DAEMCO C: Hydrants; DAEMCO D: Series 30/00 non-swab and 30/10 for swab; WSAA Appraisal 1517 (10/05/16) F: Removable Top Cap & Internal Assembly. Thermal bonded polymeric coating. Purple body and lug for recycled water.; WSAA Appraisal 1517 (10/05/16) K: All new hydrants are to be 100 mm with 100 mm flanges, 100 mm risers and spring heads
354 | DAEMCO C: Viadux; DAEMCO D: Sureflow
355 | DAEMCO C: Civil Pipe Supplies; DAEMCO D: BETTA normal & Swab
356 | DAEMCO C: AAP Industries; DAEMCO D: MAXIFLO/appFLO
357 | DAEMCO C: Derwent Industries; DAEMCO D: Derwent non-swab; WSAA Appraisal 1517 (10/05/16) K: NOT ACCEPTED BY SP
358 | DAEMCO C: Dobbie Dico; WSAA Appraisal 1517 (10/05/16) K: All new hydrants are to be 100 mm with 100 mm flanges, 100 mm risers and spring heads
359 | A: Hydrant and air valve isolator’s valves; B: No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published; DAEMCO C: AVK; DN80 to DN300 E: DN80 - DN100; WSAA Appraisal 1517 (10/05/16) F: Thermal bonded polymeric coating Min. PN16; WSAA Appraisal 1517 (10/05/16) K: Mandatory for Hydrants on Trunk Water mains >DN300 Isolator Valve for Hydrant - Min. DN100 Clockwise Opening Direction
360 | DAEMCO C: Viadux
361 | DAEMCO C: Crevet
362 | A: Valve box & cover C.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1306-1; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: Bitumen coated to AS 3750.4
363 | DAEMCO C: NIBF / Iplex
364 | DAEMCO C: Tellam
365 | DAEMCO C: Gatic / Iplex
366 | A: Hydrant box & cover C.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1306-1; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: Bitumen coated to AS 3750.4
367 | DAEMCO C: NIBF / Iplex
368 | DAEMCO C: Tellam
369 | DAEMCO C: Gatic/Iplex
370 | A: Valve & hydrant boxes (recycled plastics) & DI Covers; B: No WSA-PS Refer details on SEQ-WAT-1305-1; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: Non-trafficable location only. H - Hydrants V - Valves AV - Air valve; WSAA Appraisal 1517 (10/05/16) K: Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2209-1
371 | DAEMCO C: Crevet
372 | DAEMCO C: Vinidex
373 | A: Plastic surround to valve/hydrant boxes; B: No WSA-PS For sizes refer details on SEQ-WAT-1306-1; DAEMCO C: Replas Australia; WSAA Appraisal 1517 (10/05/16) F: Non-trafficable location only.; WSAA Appraisal 1517 (10/05/16) K: Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2209-1
374 | A: Valve extension spindles; B: 262 4.1 - DN100 to DN525/600 4.2 - Length by Design 4.3 - Valve extension spindles shall be coated with a polymeric coating to AS 4158 with 350 µm DFT (minimum), or Valve extension spindles shall be hot-dip galvanized in accordance with AS 4680. Spindle support with bearing at 1 per installation minimum and at 1.8 m max spacings; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: AS2638 Compliant
375 | DAEMCO C: NIBF / Iplex
376 | DAEMCO C: Forge Bros / Vinidex
377 | DAEMCO C: Challenger; WSAA Appraisal 1517 (10/05/16) K: Use is subject to acceptance by SP
378 | A: Flanges MS; B: 204 - Flanges 4.1 - PN16 minimum 4.2 - DN by Design subject to SP approval 4.3 - Flanged 4.4 - Seal coating for DN450 and larger 4.5 - Sintakote minimum for above ground 4.6 - Flanged at PN16 minimum 4.7 - Cathodic Protection by design 4.8 - Sintapipe lining option 4.9 - SBR & EPDM 4.10 - Sintakote minimum; DAEMCO C: Steel Mains; WSAA Appraisal 1517 (10/05/16) F: Class 16 Thermal bonded polymeric coating
379 | DAEMCO C: NIBF / Iplex
380 | A: Flange gaskets and 'O' rings; B: 312 4.1 - PN16 min or as per Design 4.2 - Gasket as Standard with O-ring for required steel flanges 4.3 - Types WA, WC and WG subject to fluid needs 4.4 - DN as per design 4.5 - Material as per Standards 4.6 - Hardness as per range in Table 2 of WSA 109-2011 4.7 - Thickness of 3.0 mm at PN16 and 1.5 mm at PN35; DAEMCO C: All WSA PS-312 compliant products are accepted
381 | A: Bolts; B: No WSA-PS Refer details on SEQ-WAT-1313-1; WSAA Appraisal 1517 (10/05/16) F: 316 Stainless steel bolts
382 | A: PE mechanical compression fittings for reduced size water mains; B: 208 DN63 2.(a) - AS/NZS4129 or EN 1254 acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE 4.4 - Flange not used 4.5 - SBR & EPDM; DAEMCO C: George Fischer; DN80 to DN300 E: DN63; WSAA Appraisal 1517 (10/05/16) F: PN16
383 | DAEMCO C: Philmac / Philmac & Vinidex
384 | DAEMCO C: Plasson
385 | DAEMCO C: Talbot
386 | DAEMCO C: Alprene
387 | DAEMCO C: Iplex
388 | DAEMCO C: Viadux
389 | A: PE Fittings (for mains and large service pipes); B: 208 DN63 and larger 2.(a) AS/NZS4129 or EN 1555 or EN 12201 or EN 13244 is acceptable. 4.1 - PN16 minimum 4.2 - Electrofusion and butt weld 4.3 - Couplings, tees, bends, elbows/adjustable elbows, end caps, stub flanges, saddles, reducers 4.4 - AS 4087 compatibility for mating flange 4.5 - SBR & EPDM; DAEMCO C: Plasson; DN80 to DN300 E: Coupler up to DN710; WSAA Appraisal 1517 (10/05/16) F: Comply with AS4129, PN16, Electrofusion fittings to be long type. Stub flanges only to be used for sizes DN450 and larger
390 | DAEMCO C: Georg Fischer; DAEMCO D: ELGEF Plus Draw - Lock
391 | DAEMCO C: Friatec / Vinidex; DAEMCO D: Frialen; DN80 to DN300 E: DN250-560 with branch DN32-90
392 | DAEMCO C: Agru; DAEMCO D: Agru; DN80 to DN300 E: Coupler up to DN630
393 | DAEMCO C: Fusion Group / FusionPlast; DAEMCO D: Fusamatic; DN80 to DN300 E: Up to DN630; WSAA Appraisal 1517 (10/05/16) K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
394 | DAEMCO C: NUPIGECO; DAEMCO D: Elofit; DN80 to DN300 E: DN20 to DN710
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
395 | A: Full face PE flanges (for reticulation sizes); B: 208 DN63 and larger 2.(a) - AS/NZS4129 or EN 12201, EN 13244 or EN 14525 acceptable Certification 4.1 - PN16 minimum 4.2 - Electrofusion or Butt Weld 4.3 - Full Face Flange Adaptor with SS316 backing ring 4.4 - AS 4087 "Figure" compatibility for mating flange 4.5 - Refer "Flange Gaskets and 'O' Rings" above; NUPIGECO C: Plasson; DN20 to DN710 E: DN80 / DN100; DN20 to DN710 F: DN90 riser with slotted flanges suit both DN80 & DN100 flanged hydrants to WSAA 98/50; DN20 to DN710 K: Use of stub flanges is subject to acceptance by SP
396 | NUPIGECO C: Iplex; DN20 to DN710 E: Up to DN355; DN20 to DN710 F: Full face full bore connections
397 | NUPIGECO C: Friatec / Vinidex; Elofit D: Frialen; DN20 to DN710 E: Up to DN180; DN20 to DN710 F: Metal insert in the flange, backing rings not required; DN20 to DN710 K: Use is subject to acceptance by SP
398 | B: 216 4.1 - PN16 minimum 4.2 - Butt Weld pipe joint with Full Face Flange Adaptor with SS316 backing ring and AS 4087 "Figure" compatibility for mating flange; NUPIGECO C: Rodney / Vinidex; Elofit D: Maxi Stub; DN20 to DN710 E: Up to DN355; DN20 to DN710 F: Full face full bore connections; DN20 to DN710 K: Use of stub flanges is subject to acceptance by SP
399 | DI Restraint fittings (for PE) - couplings, flange adaptors, tees, bends, end caps | 245 Joining to PE Pipe only 2.(a) - EN 12201, EN 13244 or EN 14525 acceptable Certification 2.(b) - Plastic fittings not permitted 4.1 - PN16 4.2 - SBR & EPDM seal options with AS 4087 "Figure" compatibility for mating flange with WSA PS 312 gasket | Hawle / Hygrade Water | System 2000 Synoflex | Up to DN630 | Restraint type, Flange adaptor up to DN355 shall be full bore connection | Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
400 | NUPIGECO C: +GF+; Elofit D: Multi/Joint 3000; DN20 to DN710 E: Up to DN355
401 | NUPIGECO C: AVK; Elofit D: Supa Plus; DN20 to DN710 E: Up to DN315
402 | NUPIGECO C: Viking Johnson / Philmac; Elofit D: AquaFast AquaGrip; DN20 to DN710 E: Up to DN630
403 | A: PE scour Tees; B: 216 4.1 - PN16 minimum 4.2 - Electrofusion/Butt Weld pipe joint with Full Face Flange Adaptor with SS316 backing ring and AS 4087 "Figure" compatibility for mating flange on outlet; NUPIGECO C: Vinidex / Rodney; DN20 to DN710 F: Comply with AS4129
404 | NUPIGECO C: Kingston Bridge / Iplex
405 | A: Air valves; B: 265 Appendix B AS 4956 Size - DN20 and Larger Class - PN16 Type of Port - Full and Reduced Port Type of Valve - As per Design Hydraulic Data - As per Design Materials - DN20 and DN25 permitted with Plastic body. All other sizes End Connections - BSP Threaded or AS 4087 Flange with "Figure" compatibility to mating Flange; NUPIGECO C: ARI Flow control; DN20 to DN710 E: DN50-DN200; DN20 to DN710 F: PN16, Double Orifice as required, Thermal bonded polymeric coating
406 | NUPIGECO C: Bermad
407 | NUPIGECO C: Vent-O-Mat
408 | NUPIGECO C: AVFI; Elofit D: DAV-MH
409 | NUPIGECO C: ISCO; Elofit D: Vent Master PX; DN20 to DN710 K: NOT ACCEPTED BY SP
410 | Non-return valves - Swing check with counterweight lever arm | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Water c) Installation - Horizontal d) Spindle - Extended e) Lever and Counterweight minimum with switches and indicators by Design j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | Min. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP
411 | NUPIGECO C: Dobbie Dico; Elofit D: Dobbie Dico; DN20 to DN710 E: DN80-DN900
412 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/25; DN20 to DN710 E: DN50
413 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/8X; DN20 to DN710 E: DN80-DN300
414 | NUPIGECO C: Challenger Valves; Elofit D: Challenger - RSSC; DN20 to DN710 E: DN80-DN375
415 | NUPIGECO C: AVFI Pty Ltd; Elofit D: AVFI - RSFC; DN20 to DN710 E: DN50-DN300
416 | A: Non-return valves - free acting (without counterweight) Swing Check; B: 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Water c) Installation - Horizontal d) Spindle - Extended j) Flanged to AS 4087 Figure B5; NUPIGECO C: HMA Valveco; Elofit D: Valmatic Swing-flex; DN20 to DN710 E: DN50 - DN600; DN20 to DN710 F: Min. PN16, Thermal bonded polymeric coating
417 | NUPIGECO C: Dobbie Dico; Elofit D: Dobbie Dico; DN20 to DN710 E: DN80-DN900; DN20 to DN710 K: Use is subject to acceptance by SP
418 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/25; DN20 to DN710 E: DN50
419 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/8X; DN20 to DN710 E: DN80-DN300
420 | NUPIGECO C: Challenger Valves; Elofit D: Challenger - RSSC; DN20 to DN710 E: DN80-DN375
421 | NUPIGECO C: AVFI Pty Ltd; Elofit D: AVFI - RSFC; DN20 to DN710 E: DN50-DN300
422 | Pressure reducing valves | 268 See Appendix B of AS5081:2008 | Bermad Water Technologies | Bermad | DN40 - DN900 | Min PN16, Thermal bonded polymeric coating | Use is subject to acceptance by SP (In PRV installations where upstream pressures can be within 50 kPa of the required downstream pressure, Plasson C valves are preferred).
423 | NUPIGECO C: Singer / HMA Valveco; Elofit D: Singer
424 | NUPIGECO C: Plasson Australia Pty Ltd; Elofit D: Plasson C-Valve
425 | NUPIGECO C: Dorot Australia Pty Ltd; Elofit D: Dorot 300 Series
426 | NUPIGECO C: Cla-Val Pacific / Challenger; Elofit D: Cla-Val; DN20 to DN710 E: DN25-DN1200
427 | Pressure sustaining valves and altitude valves | 268 See Appendix B of AS5081:2008 | Bermad Water Technologies | Bermad | DN 40 - DN900 | Min PN16, Thermal bonded polymeric coating | Use is subject to acceptance by SP
428 | NUPIGECO C: Singer / HMA Valveco; Elofit D: Singer
429 | NUPIGECO C: Dorot Australia Pty Ltd; Elofit D: Dorot 300 Series; DN20 to DN710 E: DN25-DN1200 (Sustaining)
430 | NUPIGECO C: Cla-Val Pacific / Challenger; Elofit D: Cla-Val; DN20 to DN710 E: DN-80-DN1200 (Altitude)
431 | A: PE Flex Restraint Fitting (used as puddle flange); NUPIGECO C: +GF+; DN20 to DN710 E: Up to DN1600; DN20 to DN710 F: E-F type follow manufacturer's requirements.
432 | NUPIGECO C: Plasson; DN20 to DN710 E: Fits DN160 to DN1600 PE Pipe; DN20 to DN710 F: PE100/ PE4710 resin
433 | A: Dismantling joints for Flange Pipe and Fittings; B: 201 4.1 - Fl-Fl for DJ & Fl/Sp for UniFlange 4.2 - Thrust type and non-thrust type minimum PN16 4.3 - Thrust Restraint by Fitting 4.4 - SBR & EPDM; NUPIGECO C: Viadux; DN20 to DN710 F: Thrust restraint type and non-thrust type are Flanged to AS4087 PN16. SS316 bolts, nuts and washers. Larger sizes of UniFlange shall be assessed for available Fitting PN vs Pipeline Test Head.; DN20 to DN710 K: Uni-flange to be used within pit or aboveground locations only
434 | NUPIGECO C: Viking Johnson
435 | NUPIGECO C: Valveco; Elofit D: Uni-Flange Adaptor; DN20 to DN710 E: DN50-DN500
436 | NUPIGECO C: Hygrade Water; Elofit D: Pipemate; DN20 to DN710 E: DN80-DN900
437 | NUPIGECO C: AVFI; Elofit D: AFD10 Series; DN20 to DN710 E: DN80-DN1200
438 | NUPIGECO C: AVFI; Elofit D: AFD20 Series; DN20 to DN710 E: DN80-DN1200
439 | A: Flowmeter - Network Meter; B: No WSAA PS 4.1 - Flange to AS4087 Figure 5 4.2 - PN16; NUPIGECO C: ABB; Elofit D: ABB; DN20 to DN710 K: ABB Water master
440 | NUPIGECO C: Siemens; Elofit D: Siemens; DN20 to DN710 K: Use is subject to acceptance by SP
441 | NUPIGECO C: E & H; Elofit D: E & H; DN20 to DN710 K: Use is subject to acceptance by SP
442 | NUPIGECO C: Emerson; Elofit D: Emerson
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
443 | A: Category: WATER SERVICES
444 | A: Tapping bands for DI & PVC pipes; B: 310 4.1 - DN100 to DN300 4.2 - Without Electrical Isolation 4.3 - Female Rp thread to AS ISO 7.1; Emerson C: Viadux; Emerson F: Gunmetal - Positive stops
445 | Emerson C: Gatic / Milne
446 | Emerson C: RMC
447 | Emerson C: 4N Products & Stockbrands; Emerson D: 4N; Emerson E: DN100, 150, 200; Emerson F: Positive stops, coloured blue WSAA Appraisal PA10/18
448 | A: Tapping bands for PE - mechanical; B: 327 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation; Emerson C: Gatic / Milne; Emerson E: DN63-DN315; Emerson F: Gunmetal - Positive stops Only for where E-F saddles are not practicable; Emerson K: NOT ACCEPTED BY SP
449 | Emerson C: 4N Products & Stockbrands; Emerson D: 4N; Emerson E: DN63, 90, 125 & 180; Emerson F: Positive stops, coloured black Only for where E-F saddles are not practicable WSAA Appraisal PA10/19
450 | Emerson C: Hawle / Hygrade Water; Emerson D: Haku; Emerson E: DN63 - DN315; Emerson F: Ductile iron lower half
451 | Emerson C: Hawle / Hygrade Water; Emerson D: Haku; Emerson E: DN250 - DN630; Emerson F: Stainless steel strap lower half
452 | A: Tapping saddle for PE - electrofusion; B: 329 329.2.(a) - EN Standards accepted 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Combined Saddle and Outlet off-take with integral cutter/shut off 4.4 - Without electrical Isolation; Emerson C: Plasson; Emerson E: DN63, 90, 125 & 180; Emerson F: Comply with AS4129 PN16
453 | Emerson C: George Fischer
454 | Emerson C: Friatec / Vinidex; Emerson D: Frialen
455 | Emerson C: Fusion Group / FusionPlast; Emerson D: Fusamatic; Emerson E: Up to DN355; Emerson K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
456 | A: Ferrules - TPFNR Bonnet Ferrule Cocks; B: No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN16 with ability for under pressure tapping 3 - Male R thread to AS ISO 7.1 4 - Outlet fitting PE to WSA PS 207 or Copper to WSA PS 214 5 - DN50 to include 90 degree bend with union connection to AS3688 at outlet; Emerson C: Gatic / Milne; Emerson F: Dezincification resistant material and comply with AS/NZS 3688
457 | Emerson C: Elster
458 | Emerson C: RMC
459 | A: Ball valves - Water Service; B: 274 4.1 - PN16 minimum 4.2 - Plastic not permitted, Body and Handle to be DR copper alloy 4.3 - By accepted product 4.4 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 or PE Compression 4.5 - 90 Degree closure with 38 mm handle for maintap and 50 mm handle for meter. Meter ball valve with Locking open/close function 4.6 - Water Supply Property Service; Emerson C: Gatic / Milne; Emerson F: Dezincification resistant material and comply with AS/NZS 3688; Emerson K: Ball valves must be capable of being locked by the customer with their own padlock.
460 | Emerson C: Elster
461 | Emerson C: RMC
462 | Emerson C: Zetco TOF
463 | Emerson C: Cimberio / Strongcast; Emerson D: Strongcast
464 | Emerson C: Austworld; Emerson D: LOGI VALVE
465 | A: Union stopcock; B: No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance; Emerson C: Gatic / Milne; Emerson F: 25 mm Dezincification resistant material and comply with AS/NZS 3688
466 | Emerson C: Elster
467 | Emerson C: RMC
468 | A: Slip Coupling; B: No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3565.1, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance 5 - Coupling to have 5mm to 20mm movement with locking nut; Emerson C: Elster; Emerson E: DN20 and DN25; Emerson F: Dezincification resistant material and comply with AS/NZS 3688 Shall have a locking nut to prevent moving apart or kinking between the moving parts; Emerson K: NOT ACCEPTED BY SP
469 | Emerson C: All Valve Industries; Emerson E: DN20
470 | Emerson C: RMC
471 | Emerson C: Strongcast
472 | Emerson C: Austworld
473 | A: Transition couplers; B: 208 or 247 Up to DN63 2.(a) - AS/NZS4129, EN1254 or equivalent acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE not used 4.4 - Flange not used 4.5 - SBR & EPDM; Emerson C: Plasson; Emerson F: PE electro-fusion to BSP connections Copper male fittings connecting to poly female fittings is not accepted; Emerson K: Push fitting not accepted by SP
474 | Emerson C: +GF+
475 | Emerson C: Friatec / Vinidex
476 | A: PE mechanical compression fittings for Small Diameter Water Service pipes; B: 208 or 247 DN25 to DN63 2.(a) - AS/NZS4129, EN1254 or equivalent acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE 4.4 - Flange not used 4.5 - SBR & EPDM; Emerson C: George Fischer; Emerson E: DN25 to DN63; Emerson F: PE to PE or PE to BSP PN16 Push fit type is not accepted
477 | Emerson C: Philmac / Philmac & Vinidex
478 | Emerson C: Plasson
479 | Emerson C: Elster
480 | Emerson C: Zetco TOF
481 | Emerson C: Talbot
482 | Emerson C: Alprene
483 | Emerson C: Iplex
484 | Emerson C: Viadux
485 | Emerson C: NUPIGECO; Emerson D: Elopress
486 | Emerson C: Austworld; Emerson D: Metforge; Emerson E: DN25 & DN 32; Emerson K: Use is subject to acceptance by SP
487 | A: Meters - 20 mm (direct and sub-metering applications); B: No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Tail Nut with gasket 5 - Colour and Check Valve requirements as per SEQ-SP requirements; Emerson C: Elster; Emerson D: V100 (PSM-T) (WM202PD); Emerson F: Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
488 | Emerson C: Elster; Emerson D: V200
489 | Emerson C: Itron; Emerson D: TD8
490 | Emerson C: RMC; Emerson D: WM273MRP multijet
491 | Emerson C: RMC; Emerson D: WM281MRP multijet
492 | Emerson C: GVT; Emerson D: TPWM
493 | A: Meters - 25 mm (direct and sub-metering applications); B: No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Tail Nut with gasket 5 - Colour and Check Valve requirements as per SEQ-SP requirements; Emerson C: Elster; Emerson D: V100 (PSM-T) (WM252PD); Emerson F: Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
494 | Emerson C: Elster; Emerson D: V200
495 | Emerson C: Itron; Emerson D: TD8
496 | Emerson C: RMC; Emerson D: WM271MRP multijet
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
497 | A: Meters - 32 mm (direct and sub- metering applications); B: No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Thread for attachment of a AS3565.1 Clause 2.6 (DR) Copper Alloy Oval Flange with two Bolts 5 - Colour and Check Valve requirements as per SEQ-SP requirements; RMC C: Elster; WM271MRP multijet D: V100 (PSM-T); WM271MRP multijet F: Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
498 | RMC C: Elster; WM271MRP multijet D: V200
499 | RMC C: Itron; WM271MRP multijet D: TD8
500 | RMC C: RMC; WM271MRP multijet D: MRP
501 | A: Meters - 40 mm (direct and sub- metering applications); B: No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Thread for attachment of a AS3565.1 Clause 2.6 (DR) Copper Alloy Oval Flange with two Bolts 5 - Colour and Check Valve requirements as per SEQ-SP requirements; RMC C: Elster; WM271MRP multijet D: V100 (PSM-T); WM271MRP multijet F: Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
502 | RMC C: RMC; WM271MRP multijet D: WM402MRP multijet
503 | RMC C: Itron; WM271MRP multijet D: Flostar M
504 | A: Meters - 50 mm and larger (direct and sub- metering applications); B: No WSA-PS 1 - AS 3565.1 Certified 2 - Std integral Round Flange as per AS3565.1 Clause 2.5 to AS4087 Figure B5 with four Bolts 3 - Colour and Check Valve requirements as per SEQ-SP requirements; RMC C: Elster; WM271MRP multijet D: H4000 Woltmann; WM271MRP multijet F: Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
505 | RMC C: Elster; WM271MRP multijet D: H5000 Woltmann
506 | RMC C: Arad / RMC; WM271MRP multijet D: Woltman Silver Turbo
507 | RMC C: Itron; WM271MRP multijet D: Flostar M
508 | RMC C: Itron; WM271MRP multijet D: Woltex
509 | RMC C: Sensus; WM271MRP multijet D: Meistream
510 | A: Flowmeters; B: No WSA-PS 1- Flange to AS4087 Figure 5 2- PN16; RMC C: Arad Ultrasonica / RMC; WM271MRP multijet D: Octave; WM271MRP multijet F: Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy; WM271MRP multijet K: Use is subject to acceptance by SP
511 | RMC C: Siemens Eletromagnetic; WM271MRP multijet D: Siemens
512 | RMC C: Siemens Ultrasonic; WM271MRP multijet D: Siemens
513 | RMC C: E & H Electromagnetic; WM271MRP multijet D: E & H
514 | RMC C: E & H Ultrasonic; WM271MRP multijet D: E & H
515 | RMC C: Emerson; WM271MRP multijet D: Emerson
516 | RMC C: ABB; WM271MRP multijet D: ABB; WM271MRP multijet K: Water master
517 | A: Automatic Meter Reading (AMR) Systems (sub-metering applications); B: Meter reading dials shall have between 0 kL and 10 kL of consumption showing at the time of meter supply; RMC C: Enware; WM271MRP multijet F: Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
518 | RMC C: Epitomy
519 | RMC C: Utility Technology
520 | RMC C: Halytech
521 | RMC C: Utiligy
522 | RMC C: Itron; WM271MRP multijet D: Everblu
523 | RMC C: SUMS; WM271MRP multijet D: Vivid Multi Logger
524 | A: Meter boxes; B: No WSA-PS 1 - Lids Virgin HDPE with Box Virgin and/or regrind HDPE 2 - Lid in Box at Class A to AS 3996 3 - Lid shall have a slip resistant pattern that is certified to AS/NZS4586 for Table 2 ( Class W ) and Table 5 ( Classification R11 ). 4 - Lids shall snap-lock into the box and shall include a metal device for Location and a separate 2 mm Galvanised Chain or 2 mm SS304 wire rope fixed to the lid and box. 5 - The Lid shall have moulded on it's upper surface Water Meter and shall be coloured as per SEQ-SP's requirements.; RMC C: Everhard Industries; WM271MRP multijet E: 368L * 271W * 316D (for 20 mm meters only); WM271MRP multijet F: Blue, Black or Green meter box lids; WM271MRP multijet K: Purple lid for non-drinking water meter box Black or green lid for drinking water meter box Blue lid not permitted
525 | RMC C: Everhard Industries; WM271MRP multijet E: 492L * 271W * 316D
526 | RMC C: Draper; WM271MRP multijet E: 440L * 275W * 280D
527 | RMC C: Strongcast; WM271MRP multijet E: 427L * 267W * 316D
528 | A: Single check detector check valves; B: No WSA-PS 1 - Single Check valve to AS/NZS 2845.1 2 - Fitted with compliant meters as per above; RMC C: Pentair/Viadux; WM271MRP multijet D: VALVCHEQ; WM271MRP multijet E: DN100 & DN150; WM271MRP multijet F: Model SC03. Flanged connection & spring set to 50 kPa
529 | A: Double check valve (DCV), Double check detector assembly (DCDA); B: No WSA-PS AS/NZS 2845; RMC C: Pentair/Viadux; WM271MRP multijet D: VALVCHEQ; WM271MRP multijet E: DN40, 50, 100 & 150
530 | RMC C: Bermad; WM271MRP multijet D: Cla-Val
531 | RMC C: Hydroflow Distributors; WM271MRP multijet D: Watts; WM271MRP multijet K: Use is subject to acceptance by SP
532 | A: Pre-assembled dual meter boxes; B: No WSA-PS 1 - Approved Supplier Assemblies as per SEQ-SP requirements; RMC C: Elster; WM271MRP multijet E: DN20; WM271MRP multijet F: Drinking & Drinking or Drinking & Non-drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy; WM271MRP multijet K: Use is subject to acceptance by SP
533 | RMC C: Tellam
534 | RMC C: RMC; WM271MRP multijet D: KIT235 WMKIT235
535 | Pre-assembled single meter boxes | No WSA-PS 1- approved Supplier Assemblies as per SEQ-SP requirements | Strongcast | SCMBA20 | DN20 | Drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Use is subject to acceptance by SP
536 | RMC C: Elster
537 | RMC C: Tellam
538 | RMC C: RMC; WM271MRP multijet D: KIT236 WMKIT236
539 | Sub-meter assemblies | No WSA-PS 1 - Approved Supplier Assemblies as per SEQ-SP requirements | Elster | 46492-00 | DN25 | Drinking or Non-drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Slip Coupling not accepted
540 | RMC C: Elster; WM271MRP multijet D: 46491-00; WM271MRP multijet E: DN20
541 | RMC C: Tellam
542 | RMC C: All Valve; WM271MRP multijet D: SMA20M
543 | RMC C: Strongcast; WM271MRP multijet D: SCMLIM20
544 | RMC C: Austworld; WM271MRP multijet D: SMK
545 | RMC C: RMC; WM271MRP multijet D: KIT227
546 | WM271MRP multijet D: KIT227Q
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
547 | A: Dual Check valves for Meter assemblies DN40 and Larger; B: No WSA-PS 1 - Certified to AS/NZS 2845.1 2 - Non-Testable 3 - PN16 and Flanged to AS4087 Figure B5 4 - Ductile Iron body with AS4158 coating and lining or SS316 body or SS304 body if SS316 unavailable; C: Pentair/Viadux; KIT227Q D: VALVCHEQ; KIT227Q F: Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy
548 | C: Hydroflow Distributors; KIT227Q D: Watts; KIT227Q K: Use is subject to acceptance by SP
549 | A: Reduced pressure zone device (RPZD), Reduced pressure detector assembly (RPDA); B: No WSA_PS AS/NZS 2845; C: LWG Zurn; KIT227Q D: Model 375; KIT227Q K: UW prefers RP03 RPZ
550 | C: RMC
551 | C: Pentair/Viadux; KIT227Q D: RP03
552 | C: Hydroflow Distributors; KIT227Q D: Watts; KIT227Q K: Use is subject to acceptance by SP
553 | A: Pressure Limiting Valve for Water Services; B: No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance 5 – Set point 50 m; C: RMC; KIT227Q E: DN15 – DN50; KIT227Q F: Dezincification resistant material and comply with AS/NZS 3688 Stainless Steel seat Not buried
554 | C: NEFA
555 | C: Hydroflow Distributors; KIT227Q D: Watts; KIT227Q K: Use is subject to acceptance by SP
| A | B | C | D | E | F | K | G | H | I | J
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gympie Regional Council (GRC) | Fraser Coast Regional Council (FCRC) | Bundaberg Regional Council (BRC) | North Burnett Regional Council | South Burnett Regional Council
556 | A: Category: WATER SUPPLY MISCELLANEOUS ITEMS
557 | A: Detectable marker tape; B: 318 4.1 - Tape/Product Colour - Drinking Water = Blue Non-Drinking Water = Purple. Sewerage = Cream 4.2 - Message = "Caution ASSET DESCRIPTION Buried Below" or "Danger Buried ASSET DESCRIPTION Below" 4.3 - SS 316 tracer wire 4.4 - See 4.1 above; Hydroflow Distributors C: Boddingtons
558 | Hydroflow Distributors C: Tapex
559 | Hydroflow Distributors C: LWG Zurn
560 | Hydroflow Distributors C: Rain Harvesting; Watts D: 421
561 | A: Tracer wire; B: 343 4.1 - CCS shall be AISI 1055 grade or higher 4.2 - Wire gauge Shall be 12 or thicker 4.3 - Minimum 520Kg 4.4 - Minimum 45mil 4.5 - minimum 1% 4.6 - as per standards 4.7 - as per standards 4.8 - Blue for Water Supply, Purple for Recycled Water and Cream for Pressure Sewer.; Hydroflow Distributors C: Tapex; Watts D: Copperhead; Watts E: 500, 1000 and 2500 (feet); Watts F: Approved are SoloShot EHS and SoloSHot Xtreme For HDD and Pipe bursting etc. Components of test station, connector and grounding anode are accepted
562 | A: Loose PE sleeving to DI pipe; B: 320; Hydroflow Distributors C: Viadux; Watts D: BLUEBOSS blue; Watts F: Mandatory sleeving to all DI pipe Colours are Blue for Drinking Water and Purple for Non Drinking Water to POP203
563 | Hydroflow Distributors C: Crevet
564 | A: PVC - M conduits; B: 209 4.1 - PN12 4.2 - Water Service Conduit 4.3 - Series 1 SCJ 4.4 - White for Water Conduit 4.5 - SCJ only; Hydroflow Distributors C: Vinidex; Watts D: Hydro S1; Watts F: PN12 Series 1; Use is subject to acceptance by SP K: UW requires uPVC PN9 series 1 with solvent weld joint- Refer drawing SEQ-WAT-1108-1.
565 | Hydroflow Distributors C: Iplex
566 | Hydroflow Distributors C: Viadux
567 | A: Embedment material - crushed rock; B: 351 4.1 - Single sized. 4.2 - Nominal 5 or 7 mm
568 | A: Embedment material - recycled concrete; B: 366 4.1 - Single sized 10 mm nominal 4.2 - Moisture Content by design; Hydroflow Distributors C: Queensland Recycling; Use is subject to acceptance by SP K: NOT ACCEPTED BY SP
569 | A: Bedding sand; B: AS/NZS 2566.2 Table G3 for sand.
570 | A: Concrete; B: 357 4.1 - N20 for Thrust Blocks and Unreinforced embedment. N25 for reinforced embedment 4.2 - Slumps as required for placement; Watts F: Normal class
571 | A: Security fencing; Watts F: AS1725.1 Chain Link Fabric Fencing-powder coated black; Use is subject to acceptance by SP K: In accordance with Unitywater’s specification Pr9903 – Specification for Building and Structural Works, Section 5.15 Security Fencing.
572 | A: Casing Spacers; B: 324 4.1 - Carrier pipes OD from 100mm to 1668mm 4.2 - Min space between carrier pipes and encasing pipes 50mm; Hydroflow Distributors C: kwik-ZIP; Watts D: kwik-ZIP; Watts E: HDX Series with Runner height of 38, 65, 90 and 125 mm; Watts F: For SCL, DI, PE, PVC, Concrete, GRP and FRP carrier pipes
573 | A: Plastic marker post; B: 1- Comply with Main Roads specification MRS11.14; Hydroflow Distributors C: Park International; Watts E: 1350 mm Long × 100 mm Wide × 4 mm Thick; Watts F: As per SEQ-WAT-1300-2
574 | A: Kerb Markers; B: No WSA - PS; Hydroflow Distributors C: All products meeting the specified requirements are accepted; Watts E: Brass at DN40 (cast-in) or SS at DN38 (cast-in or Pin set) with 22 high lettering; Watts F: As per SEQ-WAT-1300-1; Use is subject to acceptance by SP K: Only Brass markers accepted
575 | A: Camlock; Watts F: S/Steel 316; Use is subject to acceptance by SP K: Maximum DN100
576 | A: Category: EMERGENCY STORAGE CHAMBERS
577 | Emergency Storage Chamber | 402 2.(a) – WSA 129:2011 (or equivalent) 4.1 to 4.4 – Requirements to be specified by SEQ-SP on a case-by-case basis. | Envirotank Pty Ltd | Envirotank - Water/Wastewater Tank | From 4.8 m x 1.2 m dia. (5kl) to 16.4 m x 3.0 m dia. (110kl) | Fibreglass construction As per SEQ-SPS-1402-1 | Use Accepted - 30 Year Warranty
578 | Hydroflow Distributors C: Rocla; Watts D: Concrete Detention System; Watts E: Conc. Box units (2.4 m modules) Conc. Pipe units (2.44 m modules); Watts F: Reinforced Concrete - Sacrificial layer or Plastilined As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: UW accepts only PE lined Pipe
579 | Hydroflow Distributors C: Humes
580 | Hydroflow Distributors C: Rocla; Watts D: Plastic Detention System 'Plastream'; Watts E: 1.5 m to 2.25 m dia (10kl to 250kl); Watts F: PE spirally wound steel-reinforced pipe As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: NOT ACCEPTED BY SP
581 | Hydroflow Distributors C: Chemstore Group; Watts D: Hydrosave; Watts E: From 1.2 m to 3.5 m dia and 2.5 m to 20 m length; Watts F: Fibreglass construction As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: Use Accepted with condition of 30 Year Warranty & Providing access opening of larger size about 1200 mm opening
582 | Hydroflow Distributors C: Aquatec Fluid Systems; Watts D: Aquatec Fibreglass Storage Vessels; Watts E: From 1 m to 4 m dia and 1 m to 20 m length; Watts F: Fibreglass construction As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: Use is subject to acceptance by SP; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
583 | Hydroflow Distributors C: Tank Solutions; Watts D: Mullaly; Watts E: 1470mm to 3275mm in diameter 3.3m to 15m in length; Watts F: Fibreglass construction As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: Use is subject to acceptance by SP; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
584 | Hydroflow Distributors C: Polynex; Watts D: Polynex; Watts E: From 600mm to 3000mm in diameter; Watts F: Double walled HDPE As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: Use Accepted - Minimum 20 year warranty

## SEQ Code APAM Oct 17 (hidden)
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
2 | A: Notes: WSAA Product Specification WSAA Product Specifications are available from www.wsaa.asn.au . Section 4 of the WSAA Product Specifications is for “Agency or Project Specific Requirements”. The SEQ requirements are specified below. Manufacturer/Supplier Products may be sourced from alternative Suppliers than those listed provided that the products are manufactured by a Manufacturer whose name, and the products’ trade name, appear on the list. Size Range Size ranges need to be read in conjunction with the relevant clauses of the SEQ versions of the WSAA Codes (e.g. Water Supply Code Clause 3.1.1; Sewerage Code Clause 10.6; Pressure Sewerage Code Clause 4.5.3.1; etc.) Blank Cells In the five columns under the service provider’s names cells that are blank indicate that the product listed on that row are acceptable to the service provider. ‘Use is subject to acceptance by SP’ Contact the service provider to determine if the use of this product is acceptable in the proposed circumstance. ‘Flange’ All flanges used for pressure systems shall be PN16 or PN35 complying with AS4087.
3 | A: Category: SEWERAGE PIPES AND FITTINGS - NON PRESSURE
4 | PVC-U pipe and fittings - DWV system | 230 4.1 - Plain Wall 4.2 - Elastomeric Seal 4.3 - Stiffness as per 230.2.(c) or as required by SP 4.4 - RRJ @ SBR & EPDM | Iplex | DWV PIPE | DN100 150 225 300 375 | Plain wall only accepted | DN100 at SN6 minimum, DN150 and larger at SN8 and Moulded Fittings at SN6 minimum | DN100 at SN6 minimum, DN150 and larger at SN8 and Moulded Fittings at SN6 minimum | DN100 at SN6 minimum, DN150 and larger at SN8 and Moulded Fittings at SN6 minimum | Use is subject to acceptance by SP | DN100 at SN10, DN150 and larger at SN8 and Fittings at SN8 minimum
5 | C: Vinidex; D: DWV SEWER
6 | C: Viadux; D: D-FLO
7 | C: Micron Pipelines; D: Micron Pipelines; E: DN100 - DN300
8 | C: Pipemakers; D: Pipemakers; H: Use is subject to acceptance by SP
9 | PVC-U Pressure pipe Sewer using Standard DWV Junctions | 211 4.1 - PN12 4.2 - Deep Sewers or Minimum Cover 4.3 - Standard Packaging & Delivery 4.4 - Series 1 4.5 - RRJ @ SBR & EPDM | Iplex |  | DN150 225 300 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | NOT ACCEPTED BY SP | Mandatory for sewers deeper than 3 metres and for sewers with minimum cover All details to be confirmed with SP
10 | C: Vinidex
11 | C: Viadux
12 | DI pipe | 202S 4.1 – PN16 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – Polyurethane lining 4.4 – Restrained Joints on Zinc/Bitumen coated pipe 4.5 – Zinc/Bitumen coating or Polyurethane coating 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on all DI pipes unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | VonRoll / Reece | Ducpur/ Ecopur | DN80 - 700 | Polyurethane internal protection |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
13 |  | 200 and WSAA TN6 4.1 - PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – CAC cement lining 4.4 – Zinc/Bitumen coating 4.5 - By design 4.6 – SBR and EPDM 4.7 - PE sleeving is required on all DI pipes unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | Viadux | Tytonxtreme | DN100 - 750 | CAC cement lining | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | Use is subject to acceptance by SP | Accepted in applications where DI pipe is specified e.g. building over sewer applications | NOT ACCEPTED BY SP
14 | C: Crevet / Iplex; D: Irontite; E: DN100 - 750
15 | C: Saint-Gobain; D: Integral Zinalium; E: DN100 – 750; G: pH1 version accepted; K: Use is subject to acceptance by SP
16 | Steel pipe | 203 4.1 – By design and PN16 min 4.2 – SEQ Code nominal DN’s 4.3 – Seal coat not required for sewage 4.4 – Extra protection by design 4.5 – Joints by design to SEQ Code Standards | Steel Mains | Sintapipe |  | Internal lining would be required, either Epoxy or Sintaline |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Sintapipe accepted in applications where steel pipe is specified.
17 | A: Polypropylene (PP) pipe; B: 240 4.1 - Type B - ID Series 4.2 - SN10,000 4.3 - RRJ @ SBR & EPDM; C: Vinidex; D: SewerPRO; E: DN150 - 900; J: NOT ACCEPTED BY SP
18 | C: Iplex; D: SewerMAX; E: DN225 - 600
19 | C: Enviropipes; D: EnviroPipe; E: DN150 - 900; H: Use is subject to acceptance by SP; I: Use is subject to acceptance by SP; K: Use is subject to acceptance by SP
20 | PE pipe - NuSewers | 207 4.1 - Minimum PN8 SDR21 PE100 4.2 - Gravity Sewer fully welded 4.3 - Pipes lengths for DN160 and larger with coils accepted for DN110 4.4 - External colour light grey Solid or Striped with Internal colour white or light colour, see POP203 4.5 - PE100 only | Iplex | POLIplex | DN110 160 250 315 400 500 630 800 1000 1200 |  | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | PE is mandatory pipe for reticulation sewers, PE is preferred pipe for larger sewers. Where > PN8 is required, dark internal pipe colour may be used with prior SP approval
21 | C: Vinidex; D: Sewertech
22 | C: DMG; D: Hi-Vis
23 | C: Viadux
24 | C: Poly Pipe; D: SewerFlex
25 | C: Enviropipes; D: Enviropressure
26 | PE fittings - Moulded | 208 4.1 - PN10 preferred 4.2 - Electrofusion or butt welding 4.3 - Couplings and Saddles 4.4 - Bolting Flanges not required. 4.5 - Elastomeric Seals not permitted And Electrofusion fitting Standards AS4129, EN1555, EN12201, EN13244-4 | George Fischer / Ipex |  |  | Electrofusion fitting to be long type. | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
27 | C: Friatec / Vinidex
28 | C: Plasson; D: Lightfit
29 | C: Agru; D: AGRU
30 | C: Fusion Group/FusionPlast; D: Fusamatic; E: Up to DN630; J: Flanged tees and flanged saddles are not accepted by SP.; K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP.
31 | C: NUPIGECO; D: Elofit; E: DN110 to DN630; J: Use is subject to acceptance by SP
32 | PE fittings - Fabricated | 216 4.1 - PN10 preferred 4.2 - Electrofusion or butt welding Including Sweep Bends, MH Connectors, Sediment Traps, Tee and Bends for drop pipes and Sweep Junctions. | Vinidex |  |  | Electrofusion fitting to be long type. PE MH connectors shall have Hydrophilic seals both sides of puddle flange. | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
33 | C: Iplex
34 | VC pipe | 231 4.1 - DN100/150 Crushing Strength 34, DN225 and larger Class 160 4.2 - Sp-Soc and Sleeve Coupling 4.3 - All seal materials accepted | Hepworth | Supersleeve | DN100-1200 |  | Use is subject to acceptance by SP May only be used as jacking pipes |  |  | Use is subject to acceptance by SP May only be used as jacking pipes | May only be used as jacking pipes
35 | C: Steinzeug Keramo; D: Keramo
36 | C: Naylor / Rocla; D: Denlok
37 | A: DI IO bends or X Drop fitting; B: 201 4.1 - Sp-Soc ends to serve PVC-U DWV pipe 4.2 - Refer Standard drawings 4.3 - Standard RRJ for accept PVC-U DWV pipe 4.4 - SBR & EPDM 4.5 - Thermal-bonded polymeric coated and lined; C: Crevet; F: All Di fittings to be wrapped; J: Use is subject to acceptance by SP; K: NOT ACCEPTED BY SP
38 | C: Viadux
39 | A: Metal-banded flexible coupling; B: 235 4.1 - Need for adaptor bushes where difference between OD of pipe and ID of coupling greater than 16 mm 4.2 - Metal band and bolts shall be min SS316; C: Flex-Seal; D: Flex-Seal; E: Up to DN600
40 | C: DEKS; D: DEKS shear banded coupling; E: DN100 to DN225; I: Use is subject to acceptance by SP; J: Use is subject to acceptance by SP
41 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; C: Viadux; D: Gibault - Ezigib & Varigib; F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
42 | C: Crevet; D: Gibault & Universal
43 | C: AVK; D: Gibault & Universal
44 | C: Viking Johnson; D: MaxiFit & QuickFit
45 | C: Derwent
46 | C: DEKS; D: DEKS FLEXI-GIB; E: DN80 to DN600; I: Use is subject to acceptance by SP
47 | C: Daemco; D: Reinoversal; E: Up to DN 600
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
48 | A: Reinforced Concrete pipe; B: 233 4.1 - Class 4 4.2 - Bends not permitted 4.3 - In corrosive soils coat external face with 250 micron DFT High Build Epoxy 4.4 - Lifting holes not permitted 4.5 - 2.0 mm PE sheet Factory cast-in liner with Invert overlapped but not welded 4.6 - No additional cover 4.7 - SBR & EPDM; Daemco C: Rocla; Up to DN 600 G: Use is subject to acceptance by SP; Up to DN 600 J: Use is subject to acceptance by SP; Up to DN 600 K: Use is subject to acceptance by SP
49 | Daemco C: Humes
50 | Polycrete pipe | No WSA-PS 4.1 - Class to suit design 4.2 - Bends not permitted 4.3 - Compliance with ASTM D 6783, DIN 54815-1 and DIN 54815-2 4.4 - SBR and EPDM Sewer Pipe and Jacking Pipe approved | Iplex | Meyer pipe | DN200 to 2600 |  | Use is subject to acceptance by SP |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP Coupling Grade 316 Stainless Steel (min.)
51 | Daemco C: Global Pipe; Reinoversal D: Al Watani
52 | CC-GRP (centrifugally cast) pipe and Fittings - Sewer Pipe | 237S 4.1 - PN1 4.2 - SN10,000 minimum 4.3 - Soc-Sp RRJ 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | Sewer Pipe | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
53 | FW-GRP (filament wound) pipe and Fittings - Sewer Pipe | 205S 4.1 - As per product 4.2 - PN1 4.3 - SN10,000 minimum 4.4 - Bends, T-piece, Y-piece, Saddles, Reducers, Flanges and MH Couplings 4.5 - Soc-Sp RRJ 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Sewer Pipe | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
54 | Daemco C: Global Pipe; Reinoversal D: Fiberstrong; Up to DN 600 E: DN300 - DN4000
55 | Daemco C: Superlit / Clover Pipelines; Reinoversal D: Superlit; Up to DN 600 E: DN300 - DN3000
56 | CC-GRP (centrifugally cast) pipe and Fittings - Jacking Pipe | 205J 4.1 - As per product 4.2 - Pressure Class by design 4.3 - Stiffness Class by design 4.4 - Jacking Load by design 4.5 - 316 Stainless Steel (min) or GRP couplings 4.6 - SBR & EPDM 4.7 - Pipe Lengths to manufacturers requirements 4.8 - Standard Glass | Hobas / Global Pipe | Hobas | DN250 - DN3600 | Jacking pipes | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
57 | Daemco C: Empire Infrastructure; Reinoversal D: BOSSPIPE; Up to DN 600 E: DN300 - DN2000
58 | Daemco C: Superlit / Clover Pipelines; Reinoversal D: Superlit; Up to DN 600 E: DN400 - DN1400
59 | FW-GRP (filament wound) pipe and Fittings - Jacking Pipe | 206J 4.1 - As per product 4.2 - Pressure Class by design 4.3 - Stiffness Class by design 4.4 - Jacking Load by design 4.5 - 316 Stainless Steel (min) or GRP couplings 4.6 - SBR & EPDM 4.7 - Pipe Lengths to manufacturers requirements 4.8 - Standard Glass | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Jacking pipes |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
60 | Non-return valves | No WSA-PS | Iplex | Flap valve | DN50 to DN300 | All Di fittings to be wrapped | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
61 | Reinoversal D: Reflux valve fabricated; Up to DN 600 E: DN100
62 | Daemco C: Vinidex; Reinoversal D: Flap valve; Up to DN 600 E: DN50 to DN100
63 | Daemco C: Hygrade Water; Reinoversal D: WaStop Non-return valves; Up to DN 600 E: DN75 to DN200
64 | Daemco C: Fluid Control; Reinoversal D: Red valve - Tideflex check valves; Up to DN 600 E: DN50 to DN2400
65 | Knife gate valve - Stainless Steel | 266 4.1 - PN10 4.2 - Wafer or Lugged 4.3 - Clockwise closing, rising spindle | Pentair | Keystone | Up to DN600 | Body stainless steel Grade 316. Gate stainless steel Grade 316. Gland Follower stainless steel Grade 304 or 316. Spindle stainless steel grade 304 or 316. Yoke/Pillar/Bridge stainless steel Grade 304 or 316. Seat EPDM, NBR, RTFE or Viton. All fasteners stainless steel Grade 316. | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP |  | Subject to meeting the corrosion resistance requirements in Column F
66 | Daemco C: Challenger; Reinoversal D: Challenger
67 | Daemco C: AVFI; Reinoversal D: AVFI; Up to DN 600 J: Use is subject to acceptance by SP
68 | Daemco C: HMA Valveco; Reinoversal D: HMA Valveco
69 | Daemco C: AVK (Note: This is the only vendor complying with 316 SS throughout); Reinoversal D: AVK
70 | Knife gate valve - Fabricated Stainless Steel | 266 4.1 - PN1 4.2 - Lugged 4.3 - Clockwise closing, rising spindle (Note: This is a low pressure type gate valve, suitable only for sewer isolation etc.) | Australian Water Engineers | Australian Water Engineers | DN700 to DN1200 | Body, Gate, Gland Follower, Spindle and Yoke / Pillar / Bridge stainless steel Grade 316. Seat EPDM. All fasteners stainless steel Grade 316. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
71 | Knife gate valve - Ductile iron body | 266 4.1 - PN10 4.2 - Wafer or Lugged 4.3 - Clockwise closing, rising spindle | Pentair | Keystone | Up to DN600 | Body and Gland Follower ductile iron with fusion bonded polymeric coating external to 300 µm, internal to 350 µm (min.) or high-build two-pack epoxy to 275 µm (min.). Gate stainless steel Grade 316. Spindle stainless steel Grade 316. Yoke / Pillar / Bridge carbon steel with fusion bonded polymeric coating to 300 µm or high-build two-pack epoxy to 275 µm (min.). Seat EPDM, NBR, RTFE or Viton. All fasteners stainless steel Grade 316. All DI fittings to be wrapped | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP
72 | Daemco C: Challenger; Reinoversal D: Challenger
73 | Daemco C: AVFI; Reinoversal D: AVFI
74 | Daemco C: AVK; Reinoversal D: AVK
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
75 | A: Category: SEWERAGE PIPES AND FITTINGS - PRESSURE
76 | PVC-M pipe | 209 4.1 - PN16 4.2 - Sewer Rising main 4.3 - Series 2 only 4.4 - Cream refer POP203 4.5 - SBR & EPDM | Iplex | BLUERHINO | DN100 150 200 225 250 300 & 375 |  |  | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
77 | AVK C: Vinidex; AVK D: Hydro
78 | AVK C: Viadux; AVK D: TUF-FLO
79 | AVK C: Micron Pipelines; AVK D: Micron Pipelines; AVK E: DN100 - DN300
80 | AVK C: Pipemakers; AVK D: Pipemakers Enviromain
81 | PVC-O pipe | 210 4.1 - PN16 4.2 - MRS400 or MRS450 4.3 - Sewer Rising main 4.4 - Series 2 only, Cream refer POP203 4.5 - SBR & EPDM | Iplex | ApolloBLUE | DN100 150 200 225 250 300 & 375 |  |  |  | Use is subject to acceptance by SP | NOT ACCEPTED BY SP | Use is subject to acceptance by SP
82 | AVK C: Vinidex; AVK D: Supermain
83 | AVK C: Micron Pipelines; AVK D: Micron Pipelines; AVK E: DN100 - DN375
84 | AVK C: Pipemakers; AVK D: Alphamain; AVK E: DN100 to DN150; AVK G: Use is subject to acceptance by SP
85 | DI pipe | 200 and WSAA TN6 4.1 - All Pressure Classes - see Column F 4.2 - Seal Coat not required for Sewerage 4.3 - Cement Mortar Linings - see Columns F-K 4.4 - All fittings to be Fusion Bonded Polymeric Coated 4.5 - Restraint Joint Seals by approval 4.6 - SBR and EPDM 4.7 - PE sleeving is required on ALL DI pipes, including those with a zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | Viadux | Tytonxcel | DN250 - 750 (not 225) | PN20 | Cement Mortar lining of any type is not permitted within 5.0 metres of the HGL at pump stop. Alternative non-corrosive lining or pipe and fittings required. | Cement Mortar lining of any type is not permitted within 5.0 meters of the HGL at pump stop. Alternative non-corrosive lining or pipe and fittings required. Use of Vinidex LINX and ZAP products is subject to acceptance by SP | Cement Mortar lining of any type is not permitted within 5.0 metres of the HGL at pump stop. Alternative non-corrosive lining or pipe and fittings required. Use of Vinidex LINX and ZAP products is subject to acceptance by SP | NOT ACCEPTED BY SP | PN20 NOT ACCEPTED BY SP
86 | AVK C: Vinidex; AVK D: LINX-GP
87 | AVK C: Vinidex; AVK D: ZAP-GP
88 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: PN20, CAC lining for corrosive flows
89 | AVK C: Vinidex; AVK D: LINX-HAC
90 | AVK C: Vinidex; AVK D: ZAP-HAC
91 | AVK C: Viadux; AVK D: Tytonxcel; AVK E: DN100 150 200 250 300 375 450 500 600 & 750 (not 225); AVK F: PN35; AVK J: Use is subject to acceptance by SP; AVK K: Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials. Cement mortar lining of any type is not permitted at locations where there is a potential of the pipe lining in contact with air/gas continuously or intermittently. At such locations, non-corrosive pipes or metal pipes with non-corrosive linings shall be used. All linings of pipes and fittings at such locations shall be non-corrosive.
92 | AVK C: Crevet / Iplex; AVK D: Irontite
93 | AVK C: Vinidex; AVK D: LINX-GP
94 | AVK C: Vinidex; AVK D: ZAP-GP
95 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: PN35, CAC lining for corrosive flows
96 | AVK C: Crevet / Iplex; AVK D: Irontite
97 | AVK C: Vinidex; AVK D: LINX-HAC
98 | AVK C: Vinidex; AVK D: ZAP-HAC
99 | AVK C: Viadux; AVK D: Tytonxcel; AVK F: Flange Class
100 | AVK C: Vinidex; AVK D: LINX-GP
101 | AVK C: Vinidex; AVK D: ZAP-GP
102 | AVK C: Viadux; AVK D: Tytonxtreme; AVK F: Flange Class, CAC lining for corrosive flows
103 | AVK C: Vinidex; AVK D: LINX-HAC
104 | AVK C: Vinidex; AVK D: ZAP-HAC
105 | AVK C: Saint-Gobain; AVK D: Integral Zinalium; AVK E: DN100 – DN750 (not 225); AVK F: PN35 with CAC lining; Flange Class with CAC lining; AVK K: Use is subject to acceptance by SP
106 | DI Pipe - ISO | 202S 4.1 – K9-PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 – Polyurethane lining only 4.4 – Restrained Joints on Zinc/Bitumen coated pipe 4.5 –Only Polyurethane coating on aerial pipes 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | VonRoll / Reece | Ducpur/ Ecopur | DN80 - 700 | Polyurethane internal protection | Detector Tape for ISO Pipe spirally wound along pipe and over PE sleeve on Zinc/Bitumen pipe. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
107 | DI fittings - bends, tapers, tees/branches, connectors, risers & caps/blank ends | 201 4.1 - Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by approval 4.4 - SBR & EPDM | Viadux | Tyton Joint | Up to DN750 (not 225) | Thermal bonded polymeric coating is the standard material in WSA PS 201 and WSA PS212 All DI fittings to be wrapped |  |  |  |  | Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials. Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP.
108 | AVK C: Crevet / Iplex; AVK D: Crevet; AVK E: Up to DN750 (not 225)
109 | AVK C: Vinidex; AVK D: Superlink; AVK E: Up to DN750 (not 225)
110 | AVK C: Derwent; AVK E: Up to DN750 (not 225)
111 | AVK C: Gillies; AVK E: DN100 & DN150
112 | AVK C: Himgiri Castings/Galvin Engineering / CivilPipes; AVK D: Galvin; AVK E: DN80 to DN300
113 | AVK C: Dobbie Dico; AVK D: Dobbie; AVK E: DN100 to DN250
114 | AVK C: Mallet; AVK D: Mallet; AVK E: DN80 to DN750
115 | Bolts | No WSA-PS Refer Standard Drawing SEQ-WAT-1313-1 etc. |  |  |  | 316 Stainless steel bolts | Refer Standard Drawing | Refer Standard Drawing | Refer Standard Drawing | SS316 | Grade 316 Stainless Steel (min.)
116 | 316 SS repair and flanged off-take clamps | 313 4.1 - Type R or F by SP approval 4.2 - Pipe DN by SP approval 4.3 - Off-take DN by approval 4.4 - Min. PN16 | Crevet |  | DN100 to DN300 | Min. PN16, Flanged off-take clamps approved on DI and CI host pipes only, to Pipe manufacturers specifications | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
117 | AVK C: Viadux; AVK D: Wang; AVK E: DN100 to DN300
118 | AVK C: Cascade Control; AVK D: Rapid Clamps; AVK E: DN40 to DN350; AVK J: Use is subject to acceptance by SP
119 | AVK C: Daemco; AVK D: Norma Connect; AVK E: DN80 to DN300; AVK G: Only repair clamps accepted. For Non-PE pipes only; AVK J: Only repair clamps accepted
120 | Repair Couplings | 270 4.1 - PN16 4.2 - All pipe materials 4.3 - Short and Long Series 4.4 - Straight and Stepped 4.5 - All DN Range options 4.6 - Flange end not used 4.7 – EPDM, NBR, Neoprene And SS316 bolts, nuts and washers | Nova Siria/Hygrade Water | Duofit | DN 300 - DN2000 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
121 | Flange (DI) off-take clamps | 327 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation | Hawle / Hygrade Water | Haku | DN125 to DN355 | For use on PE pipe only, installed and commissioned in accordance with manufacturers recommendations All DI fittings to be wrapped | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
122 | Metal-banded flexible couplings - Vacuum Valve coupling use only | 235 4.1 - Need for adaptor bushes where difference between OD of pipe and ID of coupling greater than 16 mm 4.2 - Metal band and bolts shall be min SS316 | Flex-Seal | Flex-Seal | Up to DN600 |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | NOT ACCEPTED BY SP
123 | AVK C: DEKS; AVK D: DEKS shear banded coupling; AVK E: DN100 to DN225; AVK J: Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
124 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; DEKS C: Viadux; DEKS shear banded coupling D: Gibault - Ezigib & Varigib; DN100 to DN225 F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
125 | DEKS C: Crevet; DEKS shear banded coupling D: Gibault & Universal
126 | DEKS C: AVK; DEKS shear banded coupling D: Gibault & Universal
127 | DEKS C: Viking Johnson; DEKS shear banded coupling D: MaxiFit, QuickFit
128 | DEKS C: Derwent
129 | DEKS C: DEKS; DEKS shear banded coupling D: DEKS FLEXI-GIB; DN100 to DN225 E: DN80 to DN600; DN100 to DN225 I: Use is subject to acceptance by SP
130 | DEKS C: Daemco; DEKS shear banded coupling D: Reinoversal; DN100 to DN225 E: Up to DN 600
131 | DI mechanical fittings - End Thrust Restraint (Gripper Type) | 271 for DI, 245 for PE 4.1 - PN16 4.2 - DI and PE 4.3 - Short and Long Series 4.4 - Straight and Stepped and Flange Adaptor 4.5 - All DN Range options 4.6 - Flange Figure as specified with SS316 bolts, nuts and washers 4.7 - SBR & EPDM & Nitrile And SS316 bolts, nuts and washers | DI mechanical fittings - End Thrust Restraint (Gripper Type) | System 2000 for PE Synoflex PN16 Restraint for AC, PVC, DICL, SCL, PE | DN50-DN300 | All DI fittings to be wrapped |  |  |  | Only accepted for use where welded joints are not practical Use of Synoflex is not accepted on PVC and GRP pipe materials | Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations The use of gripper type fittings on AC, PVC, DI and SCL pipe is subject to acceptance by SP
132 | DEKS C: AVK; DEKS shear banded coupling D: Supa Plus Restraint for PE
133 | DEKS C: +GF+; DEKS shear banded coupling D: Multi/joint 3000 Plus restraint type for AC, PVC, DI, SCL, PE
134 | DEKS C: Viking Johnson; DEKS shear banded coupling D: Aqaufast and Aquagrip Restraint for PE; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
135 |  |  | Nova Siria/Hygrade Water | Multigrip | DN350-DN1400 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP
136 | DI flanged telescopic flexible fitting | No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published | Hawle / Hygrade Water WSA PA 12/09 | Vario | DN50 - DN200 | All DI fittings to be wrapped |  |  |  | Use is subject to acceptance by SP
137 | A: Dismantling joints for Flange Pipe and Fittings; B: 201 4.1 - Fl-Fl for DJ & Fl/Sp for UniFlange 4.2 - Thrust type and non-thrust type minimum PN16 4.3 - Thrust Restraint by Fitting 4.4 - SBR & EPDM; DEKS C: Viadux; DN100 to DN225 F: Thrust restraint type and non-thrust type are Flanged to AS4087 PN16. SS316 bolts, nuts and washers. Larger sizes of UniFlange shall be assessed for available Fitting PN vs Pipeline Test Head. All DI fittings to be wrapped; DN100 to DN225 G: Restrained type only; Use is subject to acceptance by SP K: Uni-flange to be used within pit or aboveground locations only
138 | DEKS C: Viking Johnson; DN100 to DN225 G: NOT ACCEPTED BY SP
139 | DEKS C: Valveco; DEKS shear banded coupling D: Uni-Flange Adaptor; DN100 to DN225 E: DN50-DN500; DN100 to DN225 G: Use is limited - refer to SP for advice; DN100 to DN225 I: Use is subject to acceptance by SP; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
140 | DEKS C: Hygrade Water; DEKS shear banded coupling D: Pipemate; DN100 to DN225 E: DN80-DN900; DN100 to DN225 G: NOT ACCEPTED BY SP
141 | DEKS C: AVFI; DEKS shear banded coupling D: AFD10 Series; DN100 to DN225 E: DN80-DN1200; DN100 to DN225 G: Restrained type only; DN100 to DN225 H: Restrained type only
142 | PE pipe | 207 4.1 - PN16 4.2 - Sewer Rising main 4.3 - Coil pipe permitted up to DN125 with Pipe lengths for larger DN 4.4 - Cream refer POP203 4.5 - PE100 only | Iplex | POLIplex | DN40 50 63 90 125 180 250 315 355 450 560 630 800 | For directional drilling installations, minimum SDR 9 (PN20 PE100) unless specified otherwise and install with SS316 tracer wire. Pipe wall thickness to be designed for installation forces. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | PE is preferred pipe material - PE shall be used unless specific site conditions dictate otherwise. | PE is preferred pipe material
143 | DEKS C: Vinidex; DEKS shear banded coupling D: Sewertech
144 | DEKS C: DMG; DEKS shear banded coupling D: Hi-Vis
145 | DEKS C: Viadux
146 | DEKS C: Poly Pipe; DEKS shear banded coupling D: SewerFlex
147 | DEKS C: Cromford; DEKS shear banded coupling D: Identipipe
148 | DEKS C: Enviropipes; DEKS shear banded coupling D: Enviropressure
149 | DEKS C: ACP; DEKS shear banded coupling D: ACP; Use is subject to acceptance by SP J: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
150 | PE pipe - High Stress Crack Resistant (HSCR) Polyethylene Pipe | 207, POP016 4.1 - PN16 minimum 4.2 - Sewer Rising main 4.3 - Coil pipe permitted up to DN125 with Pipe lengths for larger DN 4.4 - Cream refer POP203 4.5 - HSCR PE100 only | Iplex | Millennium HSCR PE | DN40 50 63 90 125 180 250 315 355 450 560 630 800 | For directional drilling and pipe bursting installations, minimum SDR 9 (PN20 HSCR PE100) unless specified otherwise and install with SS316 tracer wires. Pipe wall thickness to be specified as normal PE100 as such "extra" strength should be provided. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
151 | PE fittings | 208 2(a) - AS/NZS4129 or EN1555 or EN12201 or EN13244 is acceptable 4.1 - PN16 4.2 - Electrofusion and butt weld 4.3 - Couplings, Reducers, End Caps, Bends, Tees, Stub Flanges 4.4 - Flanges & SS backing rings to AS/NZS 4087 Fig B5 or B7 4.5 - SBR & EPDM | George Fischer |  |  | Electrofusion fitting to be long type. Stub flange may only to be used for DN450 and larger sizes. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
152 | DEKS C: Friatec / Vinidex; DEKS shear banded coupling D: Frialen; DN100 to DN225 E: DN63XDN32 to DN350XDN90
153 | DEKS C: Plasson
154 | DEKS C: Agru; DEKS shear banded coupling D: AGRU; DN100 to DN225 E: Up to DN630
155 | DEKS C: Fusion Group / FusionPlast; DEKS shear banded coupling D: Fusamatic; DN100 to DN225 E: Up to DN630; Use is subject to acceptance by SP J: Flanged tees and flanged saddles are not accepted by SP; Use is subject to acceptance by SP K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
156 | DEKS C: NUPIGECO; DEKS shear banded coupling D: Elofit; DN100 to DN225 E: DN20 to DN710
157 | Full face PE flanges | 208 4.1 - PN16 4.2 - Electrofusion and butt weld 4.3 - Full Face Flange with SS backing ring 4.4 - Flange standard AS/NZS 4087 B5 or B7 4.5 - SBR & EPDM | Plasson |  | DN80/DN100 | Slotted flanges & backing rings suit both DN80 and DN100 to WSAA 98/50 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use of stub flanges is subject to acceptance by SP
158 | DEKS C: Iplex; DN100 to DN225 E: Up to DN355; DN100 to DN225 F: Full bore connections
159 | DEKS C: Friatec / Vinidex; DEKS shear banded coupling D: Frialen; DN100 to DN225 E: Up to DN180; DN100 to DN225 F: Metal insert in the flange, backing rings not required; Use is subject to acceptance by SP J: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
160 |  | 216 4.1 - PN16 4.2 - Electrofusion and butt weld | Rodney / Vinidex | Maxi Stub | Up to DN355 | Full bore connection | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
161 | Steel pipe | 203 4.1 - MPa 1.6 minimum 4.2 - DN by Design subject to SP approval 4.3 - Seal Coat not required 4.4 - Sintakote minimum for above ground 4.5 - Joint requirements by Design 4.6 - Cathodic Protection by design 4.7 - Standard pressure tests 4.8 - Sintapipe lining 4.9 - SBR & EPDM 4.10 - Sintakote minimum | Steel Mains | Sintapipe | DN324 - 813 | RRJ unless otherwise approved | Use is subject to acceptance by SP DN610 minimum size | Use is subject to acceptance by SP DN610 minimum size | Use is subject to acceptance by SP DN610 minimum size | Use is subject to acceptance by SP | Use is subject to acceptance by SP
162 | Stainless Steel Pipe | No WSA-PS WSAA Materials Fact Sheet No:2 Selection of Stainless Steels WSAA Materials Fact Sheet No:3 Fabricating Stainless Steels | ASSDA accredited fabricators | N/A | DN100 - DN750 | Min. Grade 316 Min. PN16 Flange to AS4087 Fig B5 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
163 | Resilient seated gate valves, thermal bonded polymeric coating | 260 4.1 - PN16 4.2 - All End configurations accepted 4.3 - Integral By-pass on DN450 and larger (Unitywater accepts either integral or constructed by-pass as per job specification) 4.4 - Gear Box on DN600 and larger (Refer Mechanical List) 4.5 - Anti-Clockwise closing 4.6 - No requirement for spindle cap colour 4.7 - Extension Spindle to WSA PS - 262 4.8 - Spindle Cap 4.9 - SBR & EPDM | AVK | Series 57 (light type only for DN100 & 150) Series 570 Series 36/80 Series 01/71 Series 55 | Up to DN400 Up to DN400 Up to DN300 Up to DN300 DN450 to 600 | For PE pipes PE gripper Sluice Valves by Hawle E2 System 2000 or AVK Supa Plus Coupling Series 01/70 or equal Sluice Valves with PE stubs for electrofusion acceptable. Some valves may not need by-pass (check with SEQ SPs). All DI fittings to be wrapped | DN600 and larger valves shall be DeZurik Eccentric Plug Valves Use of Auslite III is subject to acceptance by SP
164 | DEKS C: Hawle; DEKS shear banded coupling D: E2; Use is subject to acceptance by SP K: Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
165 | DEKS C: Viadux; DEKS shear banded coupling D: Series 500 Auslite II Auslite III; DN100 to DN225 E: DN200 - DN300 Up to DN 400
166 | DEKS C: Karon / Challenger; DEKS shear banded coupling D: Karon; DN100 to DN225 E: DN80 - DN600
167 | DEKS C: AVFI; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
168 | DEKS C: Betta; DEKS shear banded coupling D: BETTA; DN100 to DN225 E: DN100 - DN375; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
169 | DEKS C: AAP Industries; DEKS shear banded coupling D: Maxiflo/appFLO; DN100 to DN225 E: DN80 to DN300; DN100 to DN225 F: WSAA Appraisal 11/26 Issue 2
170 | DEKS C: Derwent Industries; DEKS shear banded coupling D: Derwent; DN100 to DN225 E: DN80 - DN600; DN100 to DN225 F: WSAA Appraisal 1511
171 | DEKS C: DAEMCO; DN100 to DN225 E: DN80 to DN300; DN100 to DN225 F: WSAA Appraisal 1517 (10/05/16); Use is subject to acceptance by SP J: NOT ACCEPTED BY SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
172 | A: Ball Valves; B: 274 4.1 - PN16 4.2 - Body material: 316 stainless steel 4.3 - by product 4.4 - BSPT thread 4.5 - Clockwise closing; DAEMCO C: Pentair / Viadux; DAEMCO D: Keystone; DN80 to DN300 E: Up to DN50; WSAA Appraisal 1517 (10/05/16) F: BSPT threaded connections Sutiable for sewage
173 |  |  | AVFI | V1 Series - 1 Piece V2 Series - 2 Piece V3 Series - 3 Piece V2FH Series- Flanged | DN8 – DN50 DN8 – DN100 DN8 – DN100 DN15 - DN50 |  | Use is subject to acceptence by SP | Use is subject to acceptence by SP | Use is subject to acceptence by SP | Use is subject to acceptence by SP
174 | CC-GRP (centrifugally cast) pipe and Fittings - Sewer Pipe | 237S 4.1 - PN1 4.2 - SN10,000 minimum 4.3 - Soc-Sp RRJ 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | DI Fittings to WSA PS 201 for Tees and Bends |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP Coupling - Grade 316 Stainless Steel (min.)
175 | FW-GRP (filament wound) pipe and Fittings - Sewer Pipe | 205S 4.1 - As per product 4.2 - PN1 4.3 - SN10,000 minimum 4.4 - Bends, T-piece, Y-piece, Saddles, Reducers, Flanges and MH Couplings 4.5 - Soc-Sp RRJ 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | DI Fittings to WSA PS 201 for Tees and Bends |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP Coupling - Grade 316 Stainless Steel (min.)
176 | DAEMCO C: Global Pipe; DAEMCO D: Fiberstrong; DN80 to DN300 E: DN300 - DN4000
177 | DAEMCO C: Superlit / Clover Pipelines; DAEMCO D: Superlit; DN80 to DN300 E: DN300 - DN3000
178 | Flowmeter - Network Meter | No WSAA PS 4.1 - Flange to AS4087 Figure 5 4.2 - PN16 | ABB | ABB |  |  |  | Use is subject to acceptance by SP |  | NOT ACCEPTED BY SP | ABB Water master
179 | DAEMCO C: Siemens; DAEMCO D: Siemens; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
180 | DAEMCO C: E & H; DAEMCO D: E & H; WSAA Appraisal 1517 (10/05/16) H: E & H 53W; NOT ACCEPTED BY SP J: E & H Promag W400; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
181 | DAEMCO C: Emerson; DAEMCO D: Emerson; WSAA Appraisal 1517 (10/05/16) G: Use is subject to acceptance by SP; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP; WSAA Appraisal 1517 (10/05/16) I: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
182 | A: Category: SEWERAGE MISCELLANEOUS ITEMS
183 | Maintenance structure covers, frames and risers | 290 4.1 - DN600 4.2 - Round Solid Top ( Conc Infill - QUU only ) Sealed Type 4.3 - 600 mm Clear Opening 4.4 - Class B and Class D 4.5 - Rocking of cover in frame not permitted 4.6 - Lifting Key as per Standard Drawings 4.7 - Markings to AS3996 Clause 1.6 (a) to (f). 4.8 - No Hinge 4.9 - Standard Packaging and Delivery 4.10 - QUU require QUU cast in as per Standard Drawings 4.11 - Standard Coating 4.12 - Bolt down for Surcharge and overland flow areas, 4 x M8 (min) SS316 Bolts 4.13 - by Standards | Gatic / Milne |  |  | Refer Standard Drawings. Covers with another Service Provider's name not accepted. Use of Square and Rectangular Covers and Frames subject to SP approved based on Design needs | Concrete Infill Covers NOT ACCEPTED BY SP | Concrete Infill Covers NOT ACCEPTED BY SP | Concrete Infill Covers NOT ACCEPTED BY SP |  | Concrete Infill Covers NOT ACCEPTED BY SP
184 | C: East Jordan (Havestock)
185 | C: Webforge
186 | C: Tellam
187 | C: Durham
188 | C: Hygrade
189 | Maintenance shaft covers, frames and risers DN<=450 | 292 4.1-DN<=450 Round 4.2-DN360 min clear opening 4.3-Standard Lifting Key 4.4-Markings to AS3996 Clause 1.6 (a) to (f) 4.5-Standard packaging 4.6-No specific markings required 4.7-No bolt down required | Smartstream | Smartstream Top Hat- P8HDS |  | DI-Class D |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP
190 | C: Smartstream; D: Smartstream Top Hat- P8PEC; F: PE - Class B
191 | C: SYI Foundry/Aymroo; D: Aymroo; E: 360 mm clear opening; F: CI - Class B
192 | Maintenance hole lightweight composite lids and frames (non- corrosive) | 292 4.1-DN>=600 Round 4.2-DN600 min clear opening 4.3-Standard Lifting Key 4.4-Markings to AS3996 Clause 1.6 (a) to (f) 4.5-Standard packaging 4.6-No specific markings required 4.7-Bolt down for Surcharge and overland flow areas, 2 x M8 min SS316 Bolts | Terra Firma |  |  | Composite - Class B and D | Non-Corrosive MH lids and frames are required for Discharge Manholes and all Manholes for sewers DN300 and larger TMR approval is required on TMR roads | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
193 | C: ACO SAKU; F: Composite - Class B
194 | C: Prime Composites; F: Composite – Class B and D; K: Use is subject to acceptance by SP
195 | Emergency Storage maintenance hole cover | 290 4.1 – DN1000 4.2 – Two part round 4.3 – 920 mm Clear Opening 4.4 – Class C 4.5 – Rocking of cover in frame not permitted 4.6 – Hand grip lifting points 4.7 – No requirements 4.8 – Central Hinge not required 4.9 – Standard Packaging and Delivery 4.10 – No requirements 4.11 – No requirements 4.12 – 4 x 3/8” Allen Key SS 316 Bolts 4.13 – Nil Seat ring SS 316 | Treloar | MC1000-Manway Cover | DN900 | Class C Fabricated S/Steel grade 316 ring Nitrile gasket seal |  |  |  | Use is subject to acceptance by SP
196 | Step irons | 314 4.1 - Single Step 4.2 - Complies with Figure 5.10 of AS1657 4.3 - Steel bar internal with Plastic encapsulation or SS316 4.4 - Plastic encapsulation or SS316 4.5 - No reflectors required 4.6 - No other safety devices required | Miyama / Nextep | Miyama |  | M053 | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP |  | NOT ACCEPTED BY SP
197 | C: Aymroo; D: Aymroo
198 | C: C & C Plastics / Havestock; D: Posistep
199 | C: Industrial Steps & Ladders; D: Sure-Step
200 | Ladders | 315 4.1 - Type D - Fixed Ladder with two Stiles 4.2 - PBT, FRP, SS316, Galvanised Steel or Aluminium 4.3 - By Standards 4.4 - By Standards 4.5 - Reflectors optional 4.6 - 150 mm from CL of rung to MH wall 4.7 - By Standards 4.8 - Colour as per material 4.9 - SS 316 | Miyama / Nextep | Miyama |  | Fibre reinforced plastics (yellow). Brackets & Fasteners to be SS316 Min. Clearances for Rung Type Ladders as per AS1657 Fixed Platforms, Walkways, Stairways and Ladders - Design and Installation | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP |  | NOT ACCEPTED BY SP
201 | C: Industrial Steps & Ladders; D: Add-A-Step; F: Revised installation procedure WSAA Product Update 1- 2011, Subject to WSAA appraisal 5/11 and WSAA Product Alert 1-2010. Brackets as per manufacture specification. Fasteners to be SS316. Bright yellow.
202 | C: Galvanised Steel; F: Refer to Standard Drawings; J: Use is subject to acceptance by SP
203 | C: Stainless Steel or Aluminium; J: Aluminium not accepted
204 | Maintenance Shaft PVC | 321 4.1 - As per Standards 4.2 - As per Specifications 4.3 - As per Standards 4.4 - Inlet and Outlet at DN150 to DN225 4.5 - Configurations as shown in Standard drawings 4.6 - As per accepted product 4.7 - Inlet and Outlet Sewer connection RRJ 4.8 - Cap as shown in Standard Drawings 4.9 - As per Standard Drawings 4.10 - Connect to PCV-U DWV pipe 4.11 - Max depth 3.0 metres FSL to Invert of Sewer Pipe | Aymroo | Aymroo | DN225 PVC-U Riser Shaft | Configurations of "Central Axis" maintenance shaft (CAMS) are not accepted |  | Refer to clause 6.7.2 of the SEQ Sewerage Code | Refer to clause 6.7.2 of the SEQ Sewerage Code | NOT ACCEPTED BY SP | DN225 risers not accepted. Min DN300 risers are accepted.
205 | C: SMS; D: SMS # MS3 DN150 Only
206 | Maintenance Shafts PE | 322 4.1 - As per Standards 4.2 - As per Specifications 4.3 - As per Standards 4.4.a - Inlet and Outlet at DN150 to DN225 for PVC RIGSS 4.4.b - Inlet and Outlet at DN160 to DN250 for PE Nusewer 4.5 - Configurations as shown in Standard drawings 4.6 - As per accepted product 4.7.a - Inlet and Outlet PVC Sewer connection RRJ 4.7.b - Inlet and Outlet PE Sewer connection Electrofusion 4.8 - Cap as shown in Standard Drawings 4.9 - As per Standard Drawings 4.10 - Max depth 3.0 metres FSL to Invert of Pipe | Smartstream | Poo-Pit |  | RIGSS DN225 PVC riser shaft. Nusewer fully welded with DN250 PE risers and sewer stubs. | Approved for DN150 to DN225 RIGSS only. Refer Standard Drawing SEQ-SEW-1314 Set for other approved PE MS and MH options | Approved for DN150 RIGSS only. Refer to clause 6.7.2 of the SEQ Sewerage Code | Approved for DN150 to DN225 RIGSS only. Refer to clause 6.7.2 of the SEQ Sewerage Code. Refer Standard Drawing SEQ-SEW-1314 Set for other approved PE MS and MH options | Max depth of 5.0 meters is acceptable | DN225 risers not accepted. Min DN300 risers are accepted.
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
207 | Maintenance Shafts Polypropylene - DN425 and DN600 risers | 337, 341 4.1 – DN425 and DN600 Risers 4.2 – Polypropylene Riser 4.3 – DN425 SN4 & DN600 SN8 riser pipe 4.4A – DN425 Base with DN150 sewer 4.4B – DN600 Base with DN150/225 sewer 4.5 – In-line and bends and tees 4.6 – Base and Riser ribbed 4.7A – EPDM or SBR Ring Joints RIGSS 4.8 – No locking or relief cap 4.9 - Standard MH surround, cover and frame 4.10- Max depth 3.0 meters to Invert of Sewer Pipe | Iplex | EZIpit PA 09/01 & PA 09/1-2 |  | Refer Standard Drawings | Approved for DN150 to DN225 RIGSS only as per Cell B Base is single DN size | Refer to clause 6.7.2 of the SEQ Sewerage Code | Approved for DN150 to DN225 RIGSS only Base is single DN size Refer to clause 6.7.2 of the SEQ Sewerage Code | NOT ACCEPTED BY SP | Approved for DN150 to DN225 RIGSS only as per cell B, Base is single DN size, NOT ACCEPTED FOR NUSEWER
208 | Maintenance Shafts Polypropylene - DN225 and DN300 risers | 341 4.1 – DN225 and DN300 Risers 4.2 – PVC Riser 4.3 – SN8 riser pipe 4.4 - DN150 sewer 4.5 – In-line and bends and tees 4.6 – Base ribbed, Riser Solid Wall PVC 4.7 – EPDM or SBR Ring Joints RIGSS 4.8 –Locking relief cap as per Standard Drawings 4.9 - Standard MH surround, cover and frame 4.10- Max depth 3.0 meters to Invert of Sewer Pipe | SMS | SMS PA 09/08 parts 0 to 5 Code: MS1 Code: MS2 Code: MS5 |  | Refer Standard Drawings | Approved for DN150 RIGSS only | Approved for DN150 RIGSS only Refer to clause 6.7.2 of the SEQ Sewerage Code | Approved for DN150 RIGSS only Refer to clause 6.7.2 of the SEQ Sewerage Code | NOT ACCEPTED BY SP | Approved for DN150 RIGSS only. DN225 risers not accepted. Min DN300 risers are accepted.
209 | C: REHAU; D: OD400-GD (Type H12) OD400-RML (Type H13)
210 | Pre-cast Maintenance Holes | 323 4.1a - DN1000 minimum MH 4.1b - DN600 minimum MS 4.2 - Configurations as per Standard Drawings 4.3 - No step irons or ladders 4.4 - Elastomeric and Butyl rubber seals accepted 4.5 - Calcareous aggregates no additional cover 4.6 - No special treatments 4.7 - Base format as per SEQ SP approval 4.8 - Configurations as per Standard Drawings | Humes |  | MH and MS DN150 and DN225 sewers | Refer Standard Drawings Use for larger Sewer DN's and MH diameters is subject to acceptance by SP Max depth of DN600 MS FSL to Invert of Pipe is 3.0 meters | DN600 Pre-cast pre-benched Channel base and Bowl base Maintenance shafts approved as shown in Standard Drawings | Use of MS is subject to acceptance by SP | Use of MS is subject to acceptance by SP | NOT ACCEPTED BY SP | Pre-cast MHs accepted Use of MS is subject to acceptance by SP
211 | C: Rocla
212 | A: Pre-cast Concrete Converter Slab for Cast In-situ MHs; B: No WSA-PS Refer Standard Drawings; C: Everhard; F: Refer Standard Drawings Calcareous aggregates to be used
213 | C: Tellam
214 | Plastic Maintenance Holes | No WSA-PS Refer details of Type K1 on SEQ-SEW-1314-2 Minimum DN1000 chamber and DN600 neck | Smartstream | Smart Pit | DN150 to DN300 sewers | Refer Standard drawings Max depth FSL to Invert of Pipe is 3.0 meters |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
215 | Vent poles | 325 Project Specific outcome Product Appraisal Report PA 0906 for RPC | RPC Technologies |  |  | Refer Standard Drawings Tapered, Galvanised, height as design preferred colour: heritage or mist green | Accepted option is RPC for a GRP pole @ designed height | Accepted option is RPC for a GRP pole @ designed height | Accepted option is RPC for a GRP pole @ designed height | Use is subject to acceptance by SP | Use is subject to acceptance by SP
216 | C: Ingal EPS; J: Accepted Height 12.0 m; K: Minimum accepted Height 6.0 m
217 | A: Valve box and cover C.I. & D.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1305-2; C: Viadux; F: Refer Water Code Standard Drawings for approved Valve Box and Cover
218 | C: NIBF
219 | C: Gatic / Milne
220 | C: Tellam
221 | Loose PE sleeving to DI pipe | 320 Cream Colour to POP203 | Viadux | BLUEBOSS Cream |  | Mandatory sleeving to all DI pipe | Gravity pipe Grey colour Pressure pipe Cream colour | Gravity pipe Grey colour Pressure pipe Cream colour | Gravity pipe Grey colour Pressure pipe Cream colour
222 | C: Crevet
223 | A: Embedment material - crushed rock; B: 351 4.1 - Single sized 4.2 - Nominal 5 or 7 mm
224 | Embedment material - recycled concrete | 366 4.1 - Single sized 10 mm nominal 4.2 - Moisture Content by design | Queensland Recycling |  |  |  | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP |  | NOT ACCEPTED BY SP
225 | A: Concrete-Normal Class; B: 357 4.1 - As follows N20 Thrust Blocks N25 for reinforced embedment 4.2 - Slump as required for placement
226 | Concrete-Special Class (for Maintenance hole and for concrete in aggressive environment) | 358 4.1 - SCC40 with Fly Ash/Type SR Portland Cement ratio of 0.25 to 0.30. 4.2 - Slump as required for placement 4.3 - Calcareous aggregate at 20 mm |  |  |  |  | Cast in-situ MH's Refer details on Standard Drawings Concrete N32 minimum | Cast in-situ MH's Refer details on Standard Drawings Concrete N32 minimum | Cast in-situ MH's Refer details on Standard Drawings Concrete N32 minimum | Calcareous aggregate size to be 10mm minimum. Admixtures shall be non-chloride type | Calcareous aggregate size to be 10mm minimum. Admixtures shall be non-chloride type
227 | Gas release valves | 275 Refer Appendix B of AS4883 Size of Valve - DN50 BSP, DN50 to DN200 Flanged. Class of valve - PN16 Type of Port - Full and Reduced port Type of Valve - As per design needs Hydraulic Data - By design to AS4883 Appendix B | ARI Flow control |  | DN50-DN200 | PN16, Anti Slam as required, Thermal bonded polymeric coating or 316 Stainless steel | DN225 and larger mains to only use Vinloc- Smartvalve |  |  | See drawing SEQ-SPS-1605-1 for standard gas release valve arrangement (manual operation). When QUU requires an automatic gas release valve, Vent Master PX is accepted. Use of others is subject to acceptance.
228 | C: Bermad
229 | C: Vent-O-Mat
230 | C: Odour Technologies; D: Vinloc-Smartvalve
231 | C: AVFI; D: ARV-3-N
232 | C: ISCO; D: Vent Master PX
233 | Non-return valves - Swing check with counterweight lever arm | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Sewage c) Installation - Horizontal d) Spindle - Extended e) Lever and Counterweight minimum with switches and indicators by Design j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | MIN. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
234 | C: Dobbie Dico; D: Dobbie Dico; E: DN80-DN900
235 | C: AVK; D: AVK Swing Check Valve 41/25; E: DN50
236 | C: AVK; D: AVK Swing Check Valve 41/8X; E: DN80-DN300
237 | C: Challenger Valves; D: Challenger - RSSC; E: DN80-DN375
238 | C: AVFI Pty Ltd; D: AVFI - RSFC; E: DN50-DN300; G: NOT ACCEPTED BY SP
239 | Non-return valves - free acting (without counterweight) Swing Check | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Sewage c) Installation - Horizontal d) Spindle - Extended j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | MIN. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
240 | C: Dobbie Dico; D: Dobbie Dico; E: DN80-DN900; K: Use is subject to acceptance by SP
241 | C: AVK; D: AVK Swing Check Valve 41/25; E: DN50
242 | C: AVK; D: AVK Swing Check Valve 41/8X; E: DN80-DN300
243 | C: Challenger Valves; D: Challenger - RSSC; E: DN80-DN375
244 | C: AVFI Pty Ltd; D: AVFI - RSFC; E: DN50-DN300
245 | PVC-U Fabricated Fittings Fibreglass reinforced PVC Type 'D' junctions & fittings | 230 4.1 - Plain Wall only 4.2 - Solvent Cement joints for Fabricated assemblies with Elastomeric Seal on Fitting Socket Ends 4.3 - Pipe DN100 @ SN6 min and Pipe DN150 and larger SN8 min. Fittings SN6 min 4.4 - RRJ @ SBR & EPDM | Vinidex | Deep Sewer Junction & Reinforced Fittings such as Oblique Junctions and House Connection Bends and Inspection Tees | DN100-300 | DWV uPVC Moulded Fitting reinforced to SEQ Standards. Type D Junction from moulded fittings welded and fibreglass wrapped. 45 Deg Oblique Jn and Property Connection bends and Inspection Tees fibreglass wrapped. Fabricator has Certification to Section 6 of AS/NZS 1260 and fittings Fibreglass wrapped as shown on the drawings SEQ-SEW-1104-1 and SEQ-SEW-1105-1. |  |  |  | NOT ACCEPTED BY SP | DN100 at SN10, DN150 and larger at SN8 and Fittings at SN8 minimum
246 | C: Iplex
247 | C: Fabfit
248 | C: M.E. Christensen
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
249 | PVC-U SN8 long radius bends | 236 4.1 - SN8 minimum 4.2.1 - DN150 only, 3.0 metres radius as a heat formed bend with standard socket and spigot RRJ ends. No ovality variation permitted. 4.2.2 - DN225 only, 3.0 metres radius preferred, spigot spigot ends as a heat formed bend or as a fibreglass wrapped fabricated bend with 7.5 degree segments with 300 mm to 400 mm segment length on inside springline 4.2.3 - All long radius bends by Certified fabricators to AS/NZS 1260 Section 6 4.3 - SBR & EPDM | Vinidex | Long radius 3000 mm bends | DN150 as bent pipe & DN225 as bent or fabricated pipe | AS/NZS 1260 SN8 DN150 Bends available from 5Deg to 45Deg. DN225 and larger individually fabricated to 45Deg. |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
250 | M.E. Christensen C: Iplex
251 | M.E. Christensen C: Tri Underground
252 | M.E. Christensen C: Fabfit
253 | M.E. Christensen C: M.E. Christensen
254 | A: Detectable marker tape; B: 318 4.1 - Tape/Product Colour - Drinking Water = Blue Non-Drinking Water = Purple. Sewerage = Cream 4.2 - Message = "Caution ASSET DESCRIPTION Buried Below" or "Danger Buried ASSET DESCRIPTION Below" 4.3 - SS 316 tracer wire 4.4 - See 4.1 above; M.E. Christensen C: Boddingtons
255 | M.E. Christensen C: Tapex
256 | M.E. Christensen C: Rain Harvesting; M.E. Christensen D: 421; M.E. Christensen G: Use is subject to acceptance by SP
257 | A: Tracer wire; B: 343 4.1 - CCS shall be AISI 1055 grade or higher 4.2 - Wire gauge Shall be 12 or thicker 4.3 - Minimum 520Kg 4.4 - Minimum 45mil 4.5 - minimum 1% 4.6 - as per standards 4.7 - as per standards 4.8 - Blue for Water Supply, Purple for Recycled Water and Cream for Pressure Sewer.; M.E. Christensen C: Tapex; M.E. Christensen D: Copperhead; M.E. Christensen E: 500, 1000 and 2500 (feet); M.E. Christensen F: Approved are SoloShot EHS and SoloShot Xtreme For HDD and Pipe bursting etc. Components of test station, connector and grounding anode are accepted
258 | A: Security fencing; M.E. Christensen F: AS1725.1 Chain Link Fabric Fencing-powder coated black; M.E. Christensen G: Fence details generally to CoGC Standard Drawing 05-014; M.E. Christensen H: Fence details generally to CoGC Standard Drawing 05-014; M.E. Christensen I: Fence details generally to CoGC Standard Drawing 05-014
259 | A: Hydrophilic Seal; M.E. Christensen D: Hydrotite
260 | A: Casing Spacers; B: 324 4.1 - Carrier pipes OD from 100mm to 1668mm 4.2 - Min space between carrier pipes and encasing pipes 50mm; M.E. Christensen C: kwik-ZIP; M.E. Christensen D: kwik-ZIP; M.E. Christensen E: HDX Series with Runner height of 38, 65, 90 and 125 mm; M.E. Christensen F: For SCL, DI, PE, PVC, Concrete, GRP and FRP carrier pipes
261 | Protective lining & coating (including PE lining) | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list | Refer to Mechanical IPAM list
262 | A: Camlock; M.E. Christensen F: S/Steel 316; M.E. Christensen K: Maximum DN100
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
263 | Camlock A: Category: WATER SUPPLY PIPES - PRESSURE
264 | PVC-M pipe | 209 4.1 - PN16 4.2 - Drinking Water 4.3 - Series 2 only 4.4 - Blue 4.5 - SBR & EPDM | Iplex | Reiber Blue |  | Series 2 PN16, Min SN 10 Reiber ring accepted | PN20 PVC-M and PN35 DI/DICL are preferred pipes for carriageways and industrial/commercial areas. |  |  | Only accepted where PE is unsuitable | NOT ACCEPTED BY SP
265 | Camlock C: Vinidex; Camlock D: Hydro Blue; Camlock E: DN100 to DN300
266 | Camlock C: Viadux; Camlock D: Tuf-Flo
267 | Camlock C: Micron Pipelines; Camlock D: Micron Pipelines; Camlock E: DN100 to DN300; S/Steel 316 J: Use is subject to acceptance by SP
268 | Camlock C: Pipemakers; Camlock D: Pipemakers Enviromain; S/Steel 316 J: Only accepted where PE is unsuitable
269 | PVC-O pipe | 210 4.1 - PN16 4.2 - MRS400 or MRS450 4.3 - Water main 4.4 - Series 2 only, Blue for Drinking Water and Purple for No- Drinking Water refer POP203 4.5 - SBR & EPDM | Iplex | Apollo Blue | DN100 to DN300 | Series 2 PN16, Min SN 10 MRS400 or MRS450 |  | SP USE ONLY | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
270 | Camlock C: Vinidex; Camlock D: Supermain
271 | Camlock C: Micron Pipelines; Camlock D: Micron Pipelines; Camlock E: DN100 - DN375
272 | Camlock C: Pipemakers; Camlock D: Alphamain; Camlock E: DN100 to DN150; S/Steel 316 G: Use is subject to acceptance by SP
273 | DICL pipe | 200 4.1 - All Pressure Classes - see Column F 4.2 - As per Standards 4.3 - As per accepted product 4.4 - All fittings to be Fusion Bonded Polymeric Coated 4.5 - Restraint Joint Seals by approval 4.6 - SBR and EPDM 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | Viadux | Tytonxcel | DN250 - 750 (not 225) | PN 20 | Seal coat on pipes >= 450 PN20 - Use is subject to acceptance by SP PN20 PVC-M and PN35 DI/DICL are preferred pipes for carriageways and industrial/commercial areas. | Seal coat on pipes >= 450 PN20 - Use is subject to acceptance by SP Use of Vinidex LINX and ZAP products is subject to acceptance by SP | Seal coat on pipes >= 450 PN20 - Use is subject to acceptance by SP Use of Vinidex LINX and ZAP products is subject to acceptance by SP | NOT ACCEPTED BY SP | Seal coat on pipes >= 450 Seal coat requirement is dependant on water quality. PN20 - Use is subject to acceptance by SP Restraint joint seals not suitable for: PN20 pipe; Aboveground applications; Combining joint restraint and thrust blocks; Epoxy or fusion coated spigots (incl Tytonextreme pipe); Other manufacturers sockets or other pipe materials.
274 | Camlock C: Vinidex; Camlock D: LINX-GP
275 | Camlock C: Vinidex; Camlock D: ZAP-GP
276 | Camlock C: Viadux; Camlock D: Tytonexcel; Camlock E: Up to DN750 (not 225); S/Steel 316 F: PN 35; S/Steel 316 J: Only accepted where PE is unsuitable. Seal coating required for all sizes Use of Vinidex ZAP products is subject to acceptance by SP
277 | Camlock C: Crevet / Iplex; Camlock D: Irontite
278 | Camlock C: Vinidex; Camlock D: LINX-GP
279 | Camlock C: Vinidex; Camlock D: ZAP-GP
280 | Camlock C: Viadux; Camlock D: Flange Class; S/Steel 316 F: Flange Class
281 | Camlock C: Vinidex; Camlock D: LINX-GP
282 | Camlock C: Vinidex; Camlock D: ZAP-GP
283 | Camlock C: Saint-Gobain; Camlock D: Hydroclass Zinalium; Camlock E: DN100 – DN750 (not 225); S/Steel 316 F: PN35, Flange Class; S/Steel 316 J: Only accepted where PE is unsuitable. Seal coating required for all sizes; Maximum DN100 K: Use is subject to acceptance by SP
284 | DI Pipe - ISO | 202 4.1 – K9-PN35 4.2 – Soc-Soc & Sp-Sp & Fl-Fl & Fl-Soc/Sp 4.3 –Restrained Joints on Zinc/Bitumen coated pipe 4.4 –Polyurethane without seal coating 4.5 - Only Polyurethane coating on aerial pipes 4.6 – SBR, EPDM or NBR 4.7 - PE sleeving is required on ALL DI pipes, including those with zinc-alluminium alloy coating, unless pipe manufacturer/supplier can guarantee it is not needed following comprehensive soil testing and risk assessment | VonRoll / Reece | Ducpur/ Ecopur | DN80 - 700 | Polyurethane internal protection | Detector Tape for ISO Pipe spirally wound along pipe and over PE sleeve on Zinc/Bitumen pipe. PN20 PVC-M and PN35 DI/DICL are preferred pipes for carriageways and industrial/commercial areas. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
285 | Small DN Ductile Iron Water Main pipe at PE OD’s |  | Saint-Gobain PAM | BLUTOP | DN75-DN160 | Restrained Joints PN16 Unrestrained joints PN25 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
286 | SCL pipe | 203 4.1 - MPa 1.6 minimum 4.2 - DN by Design subject to SP approval 4.3 - Seal Coat required for DN450 and larger 4.4 - Sintakote minimum for above ground 4.5 - Joint requirements by Design 4.6 - Cathodic Protection by design 4.7 - Standard pressure tests 4.8 - Sintapipe lining option 4.9 - SBR & EPDM 4.10 - Sintakote minimum | Steel Mains | Sintakote | OD114, 168, 219, 257, 273, 324 to 2159. | Minimum thickness DN100 - 4.8 mm, >DN100 - 5 mm | Accepted for sizes >DN600 | Accepted for sizes >DN600 | Accepted for sizes >DN600 | Only accepted where PE is unsuitable | Seal Coat requirement is dependant on water quality
287 | PE pipe | 207 4.1 - PN16 SDR11 PE100 4.2 - Drinking and Non-Drinking Water 4.3 - Pipes lengths for DN160 and larger and coils accepted for DN110 and smaller 4.4 - Mains Colour Blue Solid for Drinking Water and Purple solid for Non-Drinking Water with Water Service pipe Black with Blue Stripes for Drinking Water and Purple solid for Non-Drinking Water, refer POP203. 4.5 - PE100 only | Iplex |  | OD25 32 40 50 63 90 125 180 250 315 355 450 560 630 800 | PE100 PN16 Blue colour - solid or striped for drinking water Purple colour - solid for non-drinking water For directional drilling installations, minimum SDR 9 (PN20 PE100) unless specified otherwise and install with SS316 tracer wire. Pipe wall thickness to be designed for installation forces. | 1 - Used as Water Service pipe at DN25 and DN32 recommend PE80B pipe (DN50 and DN63 by CoGC) 2 - Used as Drinking Water main at DN63 and DN110 in Dual Water Supply 3 - Used as A+ Non Drinking Water main for Cul- de-sac terminal end at DN63 in Dual Water Supply 4 - Used as Drinking Water main for Cul-de-sac terminal end at DN63 in traditional Drinking Water Reticulation | “Approved for water services and water mains <= DN63 only. Other uses, or the use of larger diameters, are subject to acceptance” | Use is subject to acceptance by SP | PE is preferred pipe material for single and dual water supply systems - PE shall be used unless specific site conditions dictate otherwise. Either solid or striped colours are permitted for single and/or dual water supply systems.
288 | Camlock C: Vinidex
289 | Camlock C: DMG
290 | Camlock C: Cromford; Camlock D: Identi-pipe
291 | Camlock C: Poly Pipe
292 | Camlock C: Viadux; Camlock D: Advantage/TYCO10
293 | Camlock C: Enviropipes; Camlock D: Enviropressure
294 | Camlock C: ACP; Camlock D: ACP; S/Steel 316 G: Use is subject to acceptance by SP; S/Steel 316 J: Use is subject to acceptance by SP; Maximum DN100 K: Use is subject to acceptance by SP
295 | PE pipe - High Stress Crack Resistant (HSCR) Polyethylene Pipe | 207, POP016 4.1 - PN16 minimum 4.2 - Drinking and Non-Drinking Water 4.3 - Pipes lengths for DN160 and larger and coils accepted for DN110 and smaller 4.4 - Mains Colour Blue Solid for Drinking Water and Purple solid for Non-Drinking Water with Water Service pipe Black with Blue Stripes for Drinking Water and Purple solid for Non-Drinking Water, refer POP203. 4.5 - HSCR PE100 only | Iplex | Millennium HSCR PE | DN25 32 40 50 63 90 125 180 250 315 355 450 560 630 800 | For directional drilling and pipe bursting installations, minimum SDR 9 (PN20 HSCR PE100) unless specified otherwise and install with SS316 tracer wires. Pipe wall thickness to be specified as normal PE100 as such "extra" strength should be provided. | 1 - Used as Water Service pipe at DN25 and DN32 recommend PE80B pipe (DN50 and DN63 by CoGC) 2 - Used as Drinking Water main at DN63 and DN110 in Dual Water Supply 3 - Used as A+ Non Drinking Water main for Cul- de-sac terminal end at DN63 in Dual Water Supply 4 - Used as Drinking Water main for Cul-de-sac terminal end at DN63 in traditional Drinking Water Reticulation | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
296 | Copper pipe | 214 4.1 - Annealed for all pipe 4.2 - Natural pipe colour | Port Kembla Copper |  |  |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP
297 | CC-GRP (centrifugally cast) pipe and Fittings - Water main | 237 4.1 - PN16 minimum 4.2 - SN 10,000 minimum 4.3 - Sp-Sp RRJ Coupling and Fl Joints 4.4 - Standard Glass 4.5 - SBR & EPDM | Superlit / Clover Pipelines | Superlit | DN400 - DN1400 | Minimum SN10000, PN16 | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP | Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
298 | FW-GRP (filament wound) pipe and Fittings - Water main | 205 4.1 - DN300 and larger 4.2 - PN16 minimum 4.3 - SN 10,000 minimum 4.4 - Standard bend forms permitted 4.5 - Sp-Sp RRJ Coupling and Fl Joints 4.6 - Standard Glass 4.7 - SBR & EPDM | Flowtite / Iplex | Flowtite | DN300 - DN3000 | Minimum SN10000, PN16 | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP DI Fittings preferred | Use is subject to acceptance by SP | Use is subject to acceptance by SP
299 | C: Global Pipe; D: Fiberstrong; E: DN300 - DN4000
300 | C: Superlit / Clover Pipelines; D: Superlit; E: DN300 - DN3000
301 | Stainless Steel Pipe | No WSA-SP WSAA Materials Fact Sheet No:2 Selection of Stainless Steels WSAA Materials Fact Sheet No:3 Fabricating Stainless Steels | ASSDA accredited fabricators | N/A | DN100 - DN750 | Min. Grade 316 Min. PN16 Flange to AS4087 Fig B5 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
302 | A: Category: WATER SUPPLY FITTINGS - PRESSURE
303 | Lightweight DI bends, tees/branches & connectors | 201 4.1 - Soc-Soc, Soc-Fl & Fl-Fl 4.2 - PN16 fittings 4.3 - By approval 4.3 - SBR & EPDM | Viadux | Auslite | DN100 & DN150 | Lightweight fittings Thermal bonded polymeric coating All DI fittings to be wrapped |  |  |  |  | Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP
304 | C: Dobbie Dico; D: Dobbie; E: DN100 to DN150
305 |  |  | Himigiri Castings/Galvin Engineering / CivilPipes | Galvin | DN100 & DN150 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP
306 | DI bends, tapers, tees/branches, connectors, risers & caps/blank ends | 201 4.1 - Soc-Soc, Sp-Sp, Fl-Fl, Soc-Sp, Soc-Fl & Sp-Fl 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by SP approval 4.4 - SBR & EPDM | Viadux | Tyton Joint | Up to DN750 | Thermal bonded polymeric coating All DI fittings to be wrapped |  |  |  |  | Use of Restrained Joint Rubber Rings (Tyton-lok) subject to acceptance by SP
307 | C: Crevet / Iplex; D: Crevet
308 | C: Vinidex; D: Superlink
309 | C: Derwent
310 | C: Gillies; E: DN100 & DN150
311 | C: Himigiri Castings/Galvin Engineering / CivilPipes; D: Galvin; E: DN80 to DN300
312 | C: Dobbie Dico; D: Dobbie; E: DN100 to DN250; H: Use is subject to acceptance by SP
313 | C: Mallet; D: Mallet; E: DN80 to DN750
314 | A: DI mechanical couplings - Non End Thrust Restraint; B: 270 4.1 - PN16 4.2 - All pipe materials except PE 4.3 - Long Series 4.4 - Straight Soc-Soc 4.5 - Stepped coupling require SP approval 4.6 - Flange end not used 4.7 - SBR & EPDM And SS316 bolts, nuts and washers; C: Viadux; D: Gibault Ezigib & Vari-Gib; F: Long type All DI fittings to be wrapped DI must have thermal bonded polymeric coating
315 | C: Crevet; D: Gibault & Universal Multigib; E: Up to DN750
316 | C: AVK; D: Gibault & Universal
317 | C: Viking Johnson; D: MaxiFit, QuickFit
318 | C: Derwent
319 | C: DEKS; D: DEKS FLEXI-GIB; E: DN80 to DN750; I: Use is subject to acceptance by SP
320 | C: Daemco; D: Reinoversal; E: Up to DN 600
321 | DI mechanical couplings - End Thrust Restraint (Gripper Type) | 271 4.1 - PN16 4.2 - DI 4.3 - Short and Long Series 4.4 - Straight and Stepped and Flange Adaptor 4.5 - All DN Range options 4.6 - Flange Figure as specified with SS316 bolts, nuts and washers 4.7 - SBR & EPDM & Nitrile And SS316 bolts, nuts and washers | Hawle / Hygrade Water | Synoflex PN16 Restraint coupling for AC, PVC, DICL, SCL | DN50-DN300 |  |  |  |  | Use of Synoflex is not accepted on PVC and GRP pipe materials | The use of gripper type fittings on AC, PVC, DI and SCL pipe subject to acceptance by SP
322 | C: +GF+; D: Multi/ joint 3000 Plus restraint type for AC, PVC, DICL, SCL
323 |  |  | Nova Siria/Hygrade Water | Multigrip for all pipe material, For PVC and PE pipes use Nova Siria reinforcing liner inside the pipe when installing multigrip | DN350-DN1400 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
324 | A: DI flanged telescopic flexible fitting; B: No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published; C: Hawle / Hygrade Water; D: Vario WSA PA 12/09; E: DN50 - DN200; J: Use is subject to acceptance by SP
325 | Small DN Ductile Iron Restraint Fittings at PE ODs |  | Saint-Gobain PAM | IZIFIT | DN75-DN160 | For use directly with PE and BLUTOP pipe. | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
326 | Pretapped connectors | 201 4.1 - Soc-Soc only 4.2 - Standard and PN16 fittings 4.3 - Restraint Joint Seals by approval 4.4 - SBR & EPDM DN100 to DN150 with 4 x 20BSP tappings at 2 per side and DN200 to DN300 1 x 50BSP tapping | Viadux | Readytap | DN100 to 300 | Thermal bonded polymeric coating DN100 to DN150 with 4 x 20BSP tappings at 2 per side and DN200 to DN300 1 x 50BSP tapping |  | SP USE ONLY
327 | C: Crevet / Iplex; D: Pretapped; E: DN100 & DN150
328 | C: Vinidex; D: Superlink; E: DN100 & DN150
329 |  |  | Himigiri Castings/Galvin Engineering / CivilPipes | Galvin | DN100 & DN150 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use is subject to acceptance by SP
330 |  | 246 4.1 – Blue or Black for DW and Purple for NDW | 4N Products & Stockbrands | Supertap | DN100 & 150 | Only used on Series 2 PVC pipe Not suitable for DI pipe WSAA Appraisal 12/18 |  | SP USE ONLY |  | Use is subject to acceptance by SP
331 | 316 SS repair clamps, flanged off- take clamps & BSP tapping clamps | 313 4.1 - Type R or F by SP approval 4.2 - Pipe DN by SP approval 4.3 - Off-take DN by approval 4.4 - Min. PN16 | Crevet | Wang | DN100 to DN300 | Min. PN16, Flanged off-take clamps approved on DI and CI host pipes only, to Pipe manufacturers specifications | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
332 | C: Viadux; D: Wang; E: DN100 to DN300
333 | C: Cascade Control; D: Rapid Clamps; E: DN40 to DN350; J: Use is subject to acceptance by SP
334 | C: Daemco; D: Norma Connect; E: DN80 to DN300; G: Only repair clamps accepted. For non-PE pipes only; J: Only repair clamps accepted
335 | Repair Couplings | 270 4.1 - PN16 4.2 - All pipe materials 4.3 - Short and Long Series 4.4 - Straight and Stepped 4.5 - All DN Range options 4.6 - Flange end not used 4.7 – EPDM, NBR, Neoprene And SS316 bolts, nuts and washers | Nova Siria/Hygrade Water | Duofit | DN 300 - DN2000 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
336 | Flange DI off-take clamps | 327 4.1 - Pipe DN63 and larger (see WSA PS 207 above) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation | Hawle/Hygrade Water | Haku | DN110 to DN355 | For use on PE pipe only, installed and commissioned in accordance with manufacturers recommendations | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
337 | Resilient Seated Gate Valves, thermal bonded polymeric coating. | 260 4.1 - PN16 4.2 - All End configurations accepted 4.3 - Integral By-pass on DN450 and larger (Unitywater accepts either integral or constructed by-pass as per job specification) 4.4 - Gear Box on DN600 and larger (refer mechanical list) 4.5 - Clockwise for opening 4.6 - No requirement for spindle cap colour 4.7 - Extension Spindle to WSA PS - 262 4.8 - Spindle Cap 4.9 - SBR & EPDM | AVK | Series 57 (light type only for DN100 & 150) Series 570 Series 36/80 Series 01/71 Series 55 | Up to DN400 Up to DN400 Up to DN300 Up to DN300 DN450 to 600 | Anchor legs approved PE Pipe ended approved Gripper ends approved | DN500 and DN600 with DN100 By-pass DN750 with DN150 By-pass Use of Sureflow Auslite III is subject to acceptance by SP
338 | C: Hawle / Hygrade Water; D: E2 FL Ends E2 System 2000 A Valve FL & SOC Ends; E: DN50 - 200 DN50 - 300 DN80 - 200; F: WSAA Appraisal 11/23 WSAA Appraisal 06/07; I: Use is subject to acceptance by SP; K: Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
339 | C: Viadux; D: Series 500 Auslite Auslite II Bayard Sureflow Auslite III; E: Up to DN600 DN80, 100 & 150 DN100 to DN300 DN50 - DN200 Up to DN 400; F: Anchor Legs approved With PE pipe tails approved; I: Use of Auslite II is subject to acceptance by SP
340 | C: Karon / Challenger; D: Karon; E: DN80 - DN600
341 | C: AVFI; J: Use is subject to acceptance by SP
342 | C: Betta; D: BETTA; E: DN100 - DN375; K: Use is subject to acceptance by SP
343 | C: AAP Industries; D: Maxiflo/appFLO; E: DN80 to DN300; F: WSAA Appraisal 11/26 Issue 2; I: Use is subject to acceptance by SP
344 | C: Derwent Industries; D: Derwent; E: DN80 - DN600; F: WSAA Appraisal 1511
345 | C: DAEMCO; E: DN80 to DN300; F: WSAA Appraisal 1517 (10/05/16); J: NOT ACCEPTED BY SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
346 | Butterfly Valves | 263 4.1- PN16 4.2- resilient seated wafer, lugged or double flanged | Pentair / Viadux | Keystone | DN50-600 for wafer/ lugged DN100-1000 double flanged | Body ductile iron with fusion bonded polymeric coating external to 300 µm, internal to 350 µm (min.) or high- build two-pack epoxy to 500 µm (min.). Disc stainless steel Grade 316. Shaft stainless steel Grade 316, 410, 420, 430 or 431. Seat EPDM. All fasteners stainless steel Grade 316. Operation Type: Lever or Gearbox. Gearbox ratio as per manufacturer’s requirement, coating – high build two-pack Epoxy 275 µm (min.) | DN100 to DN250 Property Service valves are lugged and Anti-clockwise closing hand lever operated. DN375 and larger valves are double flanged and Anti- clockwise closing gearbox operated. | Use is subject to acceptance by SP Direction of closing: Anti-clockwise | Use is subject to acceptance by SP Direction of closing: Anti-clockwise | Use is subject to acceptance by SP | Direction of closing: Clockwise Wafer or Lugged valves not accepted without prior approval
347 | DAEMCO C: Ebro; DAEMCO D: Ebro
348 | DAEMCO C: AVFI; DAEMCO D: AVFI
349 | DAEMCO C: Valveco; DAEMCO D: Valveco
350 | DAEMCO C: Iplex; DAEMCO D: AVK
351 | DAEMCO C: Challenger; DAEMCO D: Challenger; WSAA Appraisal 1517 (10/05/16) G: Accepted wafer or lugged DN50 to DN300; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
352 | DAEMCO C: Hydroflow Distributors; DAEMCO D: Watts; WSAA Appraisal 1517 (10/05/16) G: Use is subject to acceptance by SP; WSAA Appraisal 1517 (10/05/16) I: Use is subject to acceptance by SP
353 | Hydrants | 267 4.1 - DN80 and DN100 Flanges | Hydrants | Series 30/00 non-swab and 30/10 for swab |  | Removable Top Cap & Internal Assembly. Thermal bonded polymeric coating. Purple body and lug for recycled water. | DN80 Flange to A.S.4087 Fig B5 Purple Body and Lug for A+ Recycled water Swabbing type at main ends refer SEQ-WAT- 1302-1 | DN80 Flange to A.S.4087 Fig B5 Swabbing type at main ends refer SEQ-WAT- 1302-1 | DN80 Flange to A.S.4087 Fig B5 Swabbing type at main ends refer SEQ-WAT- 1302-1 | Swab type only accepted DN100 flanged to AS 4087 Fig B5. 100 mm hydrant riser shall be used. For PE system, additional to DN125, a DN90 PE riser may be used with Plasson slotted flange adaptor set. | All new hydrants are to be 100 mm with 100 mm flanges, 100 mm risers and spring heads
354 | DAEMCO C: Viadux; DAEMCO D: Sureflow
355 | DAEMCO C: Civil Pipe Supplies; DAEMCO D: BETTA normal & Swab
356 | DAEMCO C: AAP Industries; DAEMCO D: MAXIFLO/appFLO; WSAA Appraisal 1517 (10/05/16) I: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP
357 | DAEMCO C: Derwent Industries; DAEMCO D: Derwent non-swab; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP; NOT ACCEPTED BY SP K: NOT ACCEPTED BY SP
358 | DAEMCO C: Dobbie Dico; WSAA Appraisal 1517 (10/05/16) G: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP; NOT ACCEPTED BY SP K: All new hydrants are to be 100 mm with 100 mm flanges, 100 mm risers and spring heads
359 | Hydrant and air valve isolator’s valves | No WSA-PS Aligned to WSA_PS 201 and 270 with Flanges to AS 4087 Figure B5 To comply with WSA PS-201S when published | AVK |  | DN80 - DN100 | Thermal bonded polymeric coating Min. PN16 |  | DN80 Flange to AS4087 Fig B5 Swabbing type at main ends refer SEQ-WAT- 1302-1 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Mandatory for Hydrants on Trunk Water mains >DN300 Isolator Valve for Hydrant - Min. DN100 Clockwise Opening Direction
360 | DAEMCO C: Viadux
361 | DAEMCO C: Crevet
362 | A: Valve box & cover C.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1306-1; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: Bitumen coated to AS 3750.4; WSAA Appraisal 1517 (10/05/16) G: Water Service Boxes for footpath and roadway shall be as per Item 41 of 11-133 and as shown on 11-134 of meter standard drawings
363 | DAEMCO C: NIBF / Iplex
364 | DAEMCO C: Tellam
365 | DAEMCO C: Gatic / Iplex
366 | A: Hydrant box & cover C.I.; B: No WSA-PS Refer details on SEQ-WAT-1305-1 and SEQ-WAT-1306-1; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: Bitumen coated to AS 3750.4
367 | DAEMCO C: NIBF / Iplex
368 | DAEMCO C: Tellam
369 | DAEMCO C: Gatic/Iplex
370 | Valve & hydrant boxes (recycled plastics) & DI Covers | No WSA-PS Refer details on SEQ-WAT-1305-1 | Viadux |  |  | Non-trafficable location only. H - Hydrants V - Valves AV - Air valve | Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2309-1 | Coloured to SEQ-WAT-1300-1 | Coloured to SEQ-WAT-1300-1 | Coloured to SEQ-WAT-1300-1, SEQ-NDW-2122-1 and SEQ-NDW-2125-2 | Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2209-1
371 | DAEMCO C: Crevet
372 | DAEMCO C: Vinidex
373 | Plastic surround to valve/hydrant boxes | No WSA-PS For sizes refer details on SEQ-WAT-1306-1 | Replas Australia |  |  | Non-trafficable location only. | Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2309-1 | Coloured to SEQ-WAT-1300-1 | Coloured to SEQ-WAT-1300-1 | Coloured to SEQ-WAT-1300-1, SEQ-NDW-2122-1 and SEQ-NDW-2125-2 | Coloured to SEQ-WAT-1300-1 and SEQ-NDW-2209-1
374 | A: Valve extension spindles; B: 262 4.1 - DN100 to DN525/600 4.2 - Length by Design 4.3 - Valve extension spindles shall be coated with a polymeric coating to AS 4158 with 350 µm DFT (minimum), or Valve extension spindles shall be hot-dip galvanized in accordance with AS 4680. Spindle support with bearing at 1 per installation minimum and at 1.8 m max spacings; DAEMCO C: Viadux; WSAA Appraisal 1517 (10/05/16) F: AS2638 Compliant
375 | DAEMCO C: NIBF / Iplex
376 | DAEMCO C: Forge Bros / Vinidex
377 | DAEMCO C: Challenger; WSAA Appraisal 1517 (10/05/16) G: Use is subject to acceptance by SP; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP; WSAA Appraisal 1517 (10/05/16) I: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
378 | A: Flanges MS; B: 204 - Flanges 4.1 - PN16 minimum 4.2 - DN by Design subject to SP approval 4.3 - Flanged 4.4 - Seal coating for DN450 and larger 4.5 - Sintakote minimum for above ground 4.6 - Flanged at PN16 minimum 4.7 - Cathodic Protection by design 4.8 - Sintapipe lining option 4.9 - SBR & EPDM 4.10 - Sintakote minimum; DAEMCO C: Steel Mains; WSAA Appraisal 1517 (10/05/16) F: Class 16 Thermal bonded polymeric coating
379 | DAEMCO C: NIBF / Iplex
380 | A: Flange gaskets and 'O' rings; B: 312 4.1 - PN16 min or as per Design 4.2 - Gasket as Standard with O-ring for required steel flanges 4.3 - Types WA, WC and WG subject to fluid needs 4.4 - DN as per design 4.5 - Material as per Standards 4.6 - Hardness as per range in Table 2 of WSA 109-2011 4.7 - Thickness of 3.0 mm at PN16 and 1.5 mm at PN35; DAEMCO C: All WSA PS-312 compliant products are accepted
381 | A: Bolts; B: No WSA-PS Refer details on SEQ-WAT-1313-1; WSAA Appraisal 1517 (10/05/16) F: 316 Stainless steel bolts
382 | PE mechanical compression fittings for reduced size water mains | 208 DN63 2.(a) - AS/NZS4129 or EN 1254 acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE 4.4 - Flange not used 4.5 - SBR & EPDM | George Fischer |  | DN63 | PN16 | Only fittings with a Copper Alloy body and a Copper Alloy compression nut are approved for use |  | Use is subject to acceptance by SP
383 | DAEMCO C: Philmac / Philmac & Vinidex
384 | DAEMCO C: Plasson
385 | DAEMCO C: Talbot
386 | DAEMCO C: Alprene
387 | DAEMCO C: Iplex; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP
388 | DAEMCO C: Viadux
389 | PE Fittings (for mains and large service pipes) | 208 DN63 and larger 2.(a) AS/NZS4129 or EN 1555 or EN 12201 or EN 13244 is acceptable. 4.1 - PN16 minimum 4.2 - Electrofusion and butt weld 4.3 - Couplings, tees, bends, elbows/adjustable elbows, end caps, stub flanges, saddles, reducers 4.4 - AS 4087 compatibility for mating flange 4.5 - SBR & EPDM | Plasson |  | Coupler up to DN710 | Comply with AS4129, PN16, Electrofusion fittings to be long type. Stub flanges only to be used for sizes DN450 and larger | Accepted for DN63 and DN110 | Accepted for DN63 and DN110 | Accepted for DN63 and DN110
390 | DAEMCO C: Georg Fischer; DAEMCO D: ELGEF Plus Draw - Lock
391 | DAEMCO C: Friatec / Vinidex; DAEMCO D: Frialen; DN80 to DN300 E: DN250-560 with branch DN32-90
392 | DAEMCO C: Agru; DAEMCO D: Agru; DN80 to DN300 E: Coupler up to DN630; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP
393 |  |  | Fusion Group / FusionPlast | Fusamatic | Up to DN630 |  | Use is subject to acceptance by SP | Accepted for DN63 and DN110 |  | Flanged tees and flanged saddles are not accepted by SP | Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
394 | DAEMCO C: NUPIGECO; DAEMCO D: Elofit; DN80 to DN300 E: DN20 to DN710; WSAA Appraisal 1517 (10/05/16) H: Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
395 | Full face PE flanges (for reticulation sizes) | 208 DN63 and larger 2.(a) - AS/NZS4129 or EN 12201, EN 13244 or EN 14525 acceptable Certification 4.1 - PN16 minimum 4.2 - Electrofusion or Butt Weld 4.3 - Full Face Flange Adaptor with SS316 backing ring 4.4 - AS 4087 "Figure" compatibility for mating flange 4.5 - Refer "Flange Gaskets and 'O' Rings" above | Plasson |  | DN80 / DN100 | DN90 riser with slotted flanges suit both DN80 & DN100 flanged hydrants to WSAA 98/50 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use of stub flanges is subject to acceptance by SP
396 | NUPIGECO C: Iplex; DN20 to DN710 E: Up to DN355; DN20 to DN710 F: Full face full bore connections
397 | NUPIGECO C: Friatec / Vinidex; Elofit D: Frialen; DN20 to DN710 E: Up to DN180; DN20 to DN710 F: Metal insert in the flange, backing rings not required; Use is subject to acceptance by SP J: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
398 |  | 216 4.1 - PN16 minimum 4.2 - Butt Weld pipe joint with Full Face Flange Adaptor with SS316 backing ring and AS 4087 "Figure" compatibility for mating flange | Rodney / Vinidex | Maxi Stub | Up to DN355 | Full face full bore connections | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP |  | Use of stub flanges is subject to acceptance by SP
399 | DI Restraint fittings (for PE) - couplings, flange adaptors, tees, bends, end caps | 245 Joining to PE Pipe only 2.(a) - EN 12201, EN 13244 or EN 14525 acceptable Certification 2.(b) - Plastic fittings not permitted 4.1 - PN16 4.2 - SBR & EPDM seal options with AS 4087 "Figure" compatibility for mating flange with WSA PS 312 gasket | Hawle / Hygrade Water | System 2000 Synoflex | Up to DN630 | Restraint type, Flange adaptor up to DN355 shall be full bore connection |  |  |  | Only accepted for use where welded joints are not practical | Use of Hawle System 2000 is subject to acceptance in Acid Sulphate Soils and Saline coastal environmental locations.
400 | NUPIGECO C: +GF+; Elofit D: Multi/Joint 3000; DN20 to DN710 E: Up to DN355
401 | NUPIGECO C: AVK; Elofit D: Supa Plus; DN20 to DN710 E: Up to DN315
402 | NUPIGECO C: Viking Johnson / Philmac; Elofit D: AquaFast AquaGrip; DN20 to DN710 E: Up to DN630; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
403 | PE scour Tees | 216 4.1 - PN16 minimum 4.2 - Electrofusion/Butt Weld pipe joint with Full Face Flange Adaptor with SS316 backing ring and AS 4087 "Figure" compatibility for mating flange on outlet | Vinidex / Rodney |  |  | Comply with AS4129 | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
404 | NUPIGECO C: Kingston Bridge / Iplex
405 | Air valves | 265 Appendix B AS 4956 Size - DN20 and Larger Class - PN16 Type of Port - Full and Reduced Port Type of Valve - As per Design Hydraulic Data - As per Design Materials - DN20 and DN25 permitted with Plastic body. All other sizes End Connections - BSP Threaded or AS 4087 Flange with "Figure" compatibility to mating Flange | ARI Flow control |  | DN50-DN200 | PN16, Double Orifice as required, Thermal bonded polymeric coating | DN40 and DN50 BSP threaded to have Brass base | DN40 and DN50 BSP threaded to have Brass base. | DN40 and DN50 BSP threaded to have Brass base. | Use is subject to acceptance by SP
406 | NUPIGECO C: Bermad
407 | NUPIGECO C: Vent-O-Mat
408 | NUPIGECO C: AVFI; Elofit D: DAV-MH
409 | NUPIGECO C: ISCO; Elofit D: Vent Master PX; Use is subject to acceptance by SP H: NOT ACCEPTED BY SP; Use is subject to acceptance by SP I: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: NOT ACCEPTED BY SP
410 | Non-return valves - Swing check with counterweight lever arm | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Water c) Installation - Horizontal d) Spindle - Extended e) Lever and Counterweight minimum with switches and indicators by Design j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | Min. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP | Only use valves with capacity for lever arm to open and close the valve AVK and Dobbie Dico are acceptable CHALLENGER and other valves without lever arm NOT ACCEPTED BY SP | Use is subject to acceptance by SP |  | NOT ACCEPTED BY SP
411 | NUPIGECO C: Dobbie Dico; Elofit D: Dobbie Dico; DN20 to DN710 E: DN80-DN900
412 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/25; DN20 to DN710 E: DN50
413 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/8X; DN20 to DN710 E: DN80-DN300
414 | NUPIGECO C: Challenger Valves; Elofit D: Challenger - RSSC; DN20 to DN710 E: DN80-DN375; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
415 | NUPIGECO C: AVFI Pty Ltd; Elofit D: AVFI - RSFC; DN20 to DN710 E: DN50-DN300; DN20 to DN710 G: NOT ACCEPTED BY SP
416 | Non-return valves - free acting (without counterweight) Swing Check | 264 Refer Appendix B of AS4794 a) Class - PN16 min - Size by Design b) Medium - Water c) Installation - Horizontal d) Spindle - Extended j) Flanged to AS 4087 Figure B5 | HMA Valveco | Valmatic Swing-flex | DN50 - DN600 | Min. PN16, Thermal bonded polymeric coating | NOT ACCEPTED BY SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
417 | NUPIGECO C: Dobbie Dico; Elofit D: Dobbie Dico; DN20 to DN710 E: DN80-DN900; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
418 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/25; DN20 to DN710 E: DN50
419 | NUPIGECO C: AVK; Elofit D: AVK Swing Check Valve 41/8X; DN20 to DN710 E: DN80-DN300
420 | NUPIGECO C: Challenger Valves; Elofit D: Challenger - RSSC; DN20 to DN710 E: DN80-DN375; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
421 | NUPIGECO C: AVFI Pty Ltd; Elofit D: AVFI - RSFC; DN20 to DN710 E: DN50-DN300
422 | Pressure reducing valves | 268 See Appendix B of AS5081:2008 | Bermad Water Technologies | Bermad | DN40 - DN900 | Min PN16, Thermal bonded polymeric coating | Dorot 300 Series for Pressure Reducing Valve and for associated Pressure Relief Valve (Dump Valve) Dorot 200 Series or Bermad IR-43Q Valve | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP (In PRV installations where upstream pressures can be within 50 kPa of the required downstream pressure, Plasson C valves are preferred).
423 | NUPIGECO C: Singer / HMA Valveco; Elofit D: Singer
424 | NUPIGECO C: Plasson Australia Pty Ltd; Elofit D: Plasson C-Valve
425 | NUPIGECO C: Dorot Australia Pty Ltd; Elofit D: Dorot 300 Series
426 | NUPIGECO C: Cla-Val Pacific / Challenger; Elofit D: Cla-Val; DN20 to DN710 E: DN25-DN1200
427 | Pressure sustaining valves and altitude valves | 268 See Appendix B of AS5081:2008 | Bermad Water Technologies | Bermad | DN 40 - DN900 | Min PN16, Thermal bonded polymeric coating | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
428 | NUPIGECO C: Singer / HMA Valveco; Elofit D: Singer
429 | NUPIGECO C: Dorot Australia Pty Ltd; Elofit D: Dorot 300 Series; DN20 to DN710 E: DN25-DN1200 (Sustaining)
430 | NUPIGECO C: Cla-Val Pacific / Challenger; Elofit D: Cla-Val; DN20 to DN710 E: DN-80-DN1200 (Altitude)
431 | PE Flex Restraint Fitting (used as puddle flange) |  | +GF+ |  | Up to DN1600 | E-F type follow manufacturer's requirements. | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
432 | NUPIGECO C: Plasson; DN20 to DN710 E: Fits DN160 to DN1600 PE Pipe; DN20 to DN710 F: PE100/ PE4710 resin; Use is subject to acceptance by SP J: Use is subject to acceptance by SP
433 | A: Dismantling joints for Flange Pipe and Fittings; B: 201 4.1 - Fl-Fl for DJ & Fl/Sp for UniFlange 4.2 - Thrust type and non-thrust type minimum PN16 4.3 - Thrust Restraint by Fitting 4.4 - SBR & EPDM; NUPIGECO C: Viadux; DN20 to DN710 F: Thrust restraint type and non-thrust type are Flanged to AS4087 PN16. SS316 bolts, nuts and washers. Larger sizes of UniFlange shall be assessed for available Fitting PN vs Pipeline Test Head.; DN20 to DN710 G: For Mains only, restrained type only; Use is subject to acceptance by SP K: Uni-flange to be used within pit or aboveground locations only
434 | NUPIGECO C: Viking Johnson; DN20 to DN710 G: For Meter Assemblies only, restrained type only
435 |  |  | Valveco | Uni-Flange Adaptor | DN50-DN500 |  | Use is limited - refer to SP for advice | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
436 | NUPIGECO C: Hygrade Water; Elofit D: Pipemate; DN20 to DN710 E: DN80-DN900; DN20 to DN710 G: For Meter Assemblies only, restrained type only
437 | NUPIGECO C: AVFI; Elofit D: AFD10 Series; DN20 to DN710 E: DN80-DN1200; DN20 to DN710 G: For Mains only, restrained type only; Use is subject to acceptance by SP H: For Mains only, restrained type only
438 | NUPIGECO C: AVFI; Elofit D: AFD20 Series; DN20 to DN710 E: DN80-DN1200; DN20 to DN710 G: For Meter Assemblies only, restrained type only; Use is subject to acceptance by SP H: For Meter Assemblies only, restrained type only
439 | Flowmeter - Network Meter | No WSAA PS 4.1 - Flange to AS4087 Figure 5 4.2 - PN16 | ABB | ABB |  |  |  | Use is subject to acceptance by SP |  | NOT ACCEPTED BY SP | ABB Water master
440 | NUPIGECO C: Siemens; Elofit D: Siemens; Use is subject to acceptance by SP H: Use is subject to acceptance by SP; Use is subject to acceptance by SP J: NOT ACCEPTED BY SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
441 | NUPIGECO C: E & H; Elofit D: E & H; Use is subject to acceptance by SP H: E & H 53W; Use is subject to acceptance by SP J: E & H Promag W400; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
442 | NUPIGECO C: Emerson; Elofit D: Emerson; DN20 to DN710 G: Use is subject to acceptance by SP; Use is subject to acceptance by SP H: Use is subject to acceptance by SP; Use is subject to acceptance by SP I: Use is subject to acceptance by SP; Use is subject to acceptance by SP J: NOT ACCEPTED BY SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
443 | A: Category: WATER SERVICES
444 | A: Tapping bands for DI & PVC pipes; B: 310 4.1 - DN100 to DN300 4.2 - Without Electrical Isolation 4.3 - Female Rp thread to AS ISO 7.1; C: Viadux; F: Gunmetal - Positive stops; I: SP USE ONLY; J: RMC tapping band also accepted on AC pipe
445 | C: Gatic / Milne
446 | C: RMC
447 | C: 4N Products & Stockbrands; D: 4N; E: DN100, 150, 200; F: Positive stops, coloured blue WSAA Appraisal PA10/18; G: NOT ACCEPTED BY SP
448 | Tapping bands for PE - mechanical | 327 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Female Rp thread to AS ISO 7.1 4.4 - Without electrical Isolation | Gatic / Milne |  | DN63-DN315 | Gunmetal - Positive stops Only for where E-F saddles are not practicable | NOT ACCEPTED BY SP |  | SP USE ONLY |  | NOT ACCEPTED BY SP
449 | C: 4N Products & Stockbrands; D: 4N; E: DN63, 90, 125 & 180; F: Positive stops, coloured black Only for where E-F saddles are not practicable WSAA Appraisal PA10/19
450 | C: Hawle / Hygrade Water; D: Haku; E: DN63 - DN315; F: Ductile iron lower half; H: Use is subject to acceptance by SP
451 | C: Hawle / Hygrade Water; D: Haku; E: DN250 - DN630; F: Stainless steel strap lower half; J: NOT ACCEPTED BY SP
452 | Tapping saddle for PE - electrofusion | 329 329.2.(a) - EN Standards accepted 4.1 - Pipe DN63 and larger ( see WSA PS 207 above ) - Off- take ID 20 mm minimum 4.2 - PN16 4.3 - Combined Saddle and Outlet off-take with integral cutter/shut off 4.4 - Without electrical Isolation | Plasson |  | DN63, 90, 125 & 180 | Comply with AS4129 PN16 | Accepted for DN63 and DN110 | SP USE ONLY | Accepted for DN63 and DN110
453 | C: George Fischer
454 | C: Friatec / Vinidex; D: Frialen
455 | C: Fusion Group / FusionPlast; D: Fusamatic; E: Up to DN355; G: Use is subject to acceptance by SP; J: Flanged saddles are not accepted by SP; K: Spigot ended fittings, flanged tees and flanged saddles are not accepted by SP
456 | A: Ferrules - TPFNR Bonnet Ferrule Cocks; B: No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN16 with ability for under pressure tapping 3 - Male R thread to AS ISO 7.1 4 - Outlet fitting PE to WSA PS 207 or Copper to WSA PS 214 5 - DN50 to include 90 degree bend with union connection to AS3688 at outlet; C: Gatic / Milne; F: Dezincification resistant material and comply with AS/NZS 3688; I: SP USE ONLY
457 | C: Elster
458 | C: RMC
459 | Ball valves - Water Service | 274 4.1 - PN16 minimum 4.2 - Plastic not permitted, Body and Handle to be DR copper alloy 4.3 - By accepted product 4.4 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 or PE Compression 4.5 - 90 Degree closure with 38 mm handle for maintap and 50 mm handle for meter. Meter ball valve with Locking open/close function 4.6 - Water Supply Property Service | Gatic / Milne |  |  | Dezincification resistant material and comply with AS/NZS 3688 | Accepted for DN20 & DN25 Ball Valves with integral PE connections shall have a Copper Alloy body and a Copper Alloy compression nut for the pipe connection | Accepted for DN20 and DN25 at meter end of services | Accepted for DN20 & DN25 |  | Ball valves must be capable of being locked by the customer with their own padlock.
460 | C: Elster
461 | C: RMC
462 | C: Zetco TOF
463 | C: Cimberio / Strongcast; D: Strongcast; H: Use is subject to acceptance by SP
464 | C: Austworld; D: LOGI VALVE; H: Accepted for DN20 and DN25 at meter end of services
465 | Union stopcock | No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance | Gatic / Milne |  |  | 25 mm Dezincification resistant material and comply with AS/NZS 3688 | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
466 | C: Elster
467 | C: RMC
468 | Slip Coupling | No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3565.1, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance 5 - Coupling to have 5mm to 20mm movement with locking nut | Elster |  | DN20 and DN25 | Dezincification resistant material and comply with AS/NZS 3688 Shall have a locking nut to prevent moving apart or kinking between the moving parts |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP
469 | C: All Valve Industries; E: DN20
470 | C: RMC
471 | C: Strongcast
472 | C: Austworld
473 | A: Transition couplers; B: 208 or 247 Up to DN63 2.(a) - AS/NZS4129, EN1254 or equivalent acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE not used 4.4 - Flange not used 4.5 - SBR & EPDM; C: Plasson; F: PE electro-fusion to BSP connections Copper male fittings connecting to poly female fittings is not accepted; K: Push fitting not accepted by SP
474 | C: +GF+
475 | C: Friatec / Vinidex; H: Use is subject to acceptance by SP; I: Use is subject to acceptance by SP; J: Use is subject to acceptance by SP
476 | PE mechanical compression fittings for Small Diameter Water Service pipes | 208 or 247 DN25 to DN63 2.(a) - AS/NZS4129, EN1254 or equivalent acceptable Certification 4.1 - PN16 minimum 4.2 - Mechanical Polyethylene or Copper Alloy both with approved Plastic grippers/olives/thimbles 4.3.1 - Transition - PE to Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4.3.2 - Coupling - PE to PE 4.4 - Flange not used 4.5 - SBR & EPDM | George Fischer |  | DN25 to DN63 | PE to PE or PE to BSP PN16 Push fit type is not accepted | Only fittings with a Copper Alloy body and a Copper Alloy compression nut are approved for use |  | Use is subject to acceptance by SP
477 | C: Philmac / Philmac & Vinidex
478 | C: Plasson
479 | C: Elster
480 | C: Zetco TOF; I: Use is subject to acceptance by SP
481 | C: Talbot
482 | C: Alprene
483 | C: Iplex; H: Use is subject to acceptance by SP; J: Use is subject to acceptance by SP
484 | C: Viadux
485 | C: NUPIGECO; D: Elopress; G: Use is subject to acceptance by SP
486 | C: Austworld; D: Metforge; E: DN25 & DN 32; J: PE pipe stands not accepted by SP; K: Use is subject to acceptance by SP
487 | Meters - 20 mm (direct and sub-metering applications) | No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Tail Nut with gasket 5 - Colour and Check Valve requirements as per SEQ-SP requirements | Elster | V100 (PSM-T) (WM202PD) |  | Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy |  |  | Use is subject to acceptance by SP | Only accepted for above ground installation
488 | C: Elster; D: V200
489 | C: Itron; D: TD8
490 | C: RMC; D: WM273MRP multijet; G: Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters.; J: NOT ACCEPTED BY SP
491 | C: RMC; D: WM281MRP multijet
492 | C: GVT; D: TPWM; G: NOT ACCEPTED BY SP
493 | Meters - 25 mm (direct and sub-metering applications) | No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Tail Nut with gasket 5 - Colour and Check Valve requirements as per SEQ-SP requirements | Elster | V100 (PSM-T) (WM252PD) |  | Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy |  |  | Use is subject to acceptance by SP | Only accepted for above ground installation
494 | C: Elster; D: V200
495 | C: Itron; D: TD8
496 | C: RMC; D: WM271MRP multijet; G: Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters.; J: NOT ACCEPTED BY SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
497 | Meters - 32 mm (direct and sub- metering applications) | No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Thread for attachment of a AS3565.1 Clause 2.6 (DR) Copper Alloy Oval Flange with two Bolts 5 - Colour and Check Valve requirements as per SEQ-SP requirements | Elster | V100 (PSM-T) |  | Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | NOT ACCEPTED BY SP |  | Use is subject to acceptance by SP
498 | RMC C: Elster; WM271MRP multijet D: V200
499 | RMC C: Itron; WM271MRP multijet D: TD8
500 | RMC C: RMC; WM271MRP multijet D: MRP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
501 | Meters - 40 mm (direct and sub- metering applications) | No WSA-PS 1 - NSC/NMI Pattern Approved 2 - AS 3565.1 Certified 3 - Integral Strainer 4 - Std Thread for attachment of a AS3565.1 Clause 2.6 (DR) Copper Alloy Oval Flange with two Bolts 5 - Colour and Check Valve requirements as per SEQ-SP requirements | Elster | V100 (PSM-T) |  | Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy |  |  | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
502 | RMC C: RMC; WM271MRP multijet D: WM402MRP multijet; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters.
503 | RMC C: Itron; WM271MRP multijet D: Flostar M; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Horizontal orientation only
504 | Meters - 50 mm and larger (direct and sub- metering applications) | No WSA-PS 1 - AS 3565.1 Certified 2 - Std integral Round Flange as per AS3565.1 Clause 2.5 to AS4087 Figure B5 with four Bolts 3 - Colour and Check Valve requirements as per SEQ-SP requirements | Elster | H4000 Woltmann |  | Purple body for non-drinking water Accuracy Class 2 Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy |  |  | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
505 | RMC C: Elster; WM271MRP multijet D: H5000 Woltmann; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Above ground installation with external top accessible (basket type) inline strainers
506 | RMC C: Arad / RMC; WM271MRP multijet D: Woltman Silver Turbo; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Horizontal orientation only; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
507 | RMC C: Itron; WM271MRP multijet D: Flostar M; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Above ground installation with external top accessible (basket type) inline strainers
508 | RMC C: Itron; WM271MRP multijet D: Woltex; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
509 | RMC C: Sensus; WM271MRP multijet D: Meistream; NOT ACCEPTED BY SP J: Only accept Meistream Plus meter installed above ground with external top accessible (basket type) inline strainers
510 | Flowmeters | No WSA-PS 1- Flange to AS4087 Figure 5 2- PN16 | Arad Ultrasonica / RMC | Octave |  | Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Arad Octave Ultrasonic and Siemens Sitrans FM Mag 8000 acceptable | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
511 | RMC C: Siemens Eletromagnetic; WM271MRP multijet D: Siemens; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Siemens Mag 8000 Advanced; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
512 | RMC C: Siemens Ultrasonic; WM271MRP multijet D: Siemens; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
513 | RMC C: E & H Electromagnetic; WM271MRP multijet D: E & H; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: E & H Promag 53W; NOT ACCEPTED BY SP J: E & H Promag W400; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
514 | RMC C: E & H Ultrasonic; WM271MRP multijet D: E & H; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
515 | RMC C: Emerson; WM271MRP multijet D: Emerson; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
516 | RMC C: ABB; WM271MRP multijet D: ABB; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP; NOT ACCEPTED BY SP K: Water master
517 | A: Automatic Meter Reading (AMR) Systems (sub-metering applications); B: Meter reading dials shall have between 0 kL and 10 kL of consumption showing at the time of meter supply; RMC C: Enware; WM271MRP multijet F: Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Hard-wired systems only. Only Elster Reed Switches to be used. One DER (digital electronic read outs) panel per building.; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
518 | RMC C: Epitomy
519 | RMC C: Utility Technology
520 | RMC C: Halytech; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: NOT ACCEPTED BY SP; NOT ACCEPTED BY SP J: Only Reed switches from the meter manufacturer and repeaters supplied from the AMR supplier are accepted
521 | RMC C: Utiligy; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
522 | RMC C: Itron; WM271MRP multijet D: Everblu; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP
523 | RMC C: SUMS; WM271MRP multijet D: Vivid Multi Logger; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP
524 | Meter boxes | No WSA-PS 1 - Lids Virgin HDPE with Box Virgin and/or regrind HDPE 2 - Lid in Box at Class A to AS 3996 3 - Lid shall have a slip resistant pattern that is certified to AS/NZS4586 for Table 2 ( Class W ) and Table 5 ( Classification R11 ). 4 - Lids shall snap-lock into the box and shall include a metal device for Location and a separate 2 mm Galvanised Chain or 2 mm SS304 wire rope fixed to the lid and box. 5 - The Lid shall have moulded on it's upper surface Water Meter and shall be coloured as per SEQ-SP's requirements. | Everhard Industries |  | 368L * 271W * 316D (for 20 mm meters only) | Blue, Black or Green meter box lids | Blue Lid not permitted | Blue Lid not permitted | Blue Lid not permitted | NOT ACCEPTED BY SP | Purple lid for non-drinking water meter box Black or green lid for drinking water meter box Blue lid not permitted
525 | RMC C: Everhard Industries; WM271MRP multijet E: 492L * 271W * 316D; NOT ACCEPTED BY SP J: Solid purple lid with non-drinking water symbol and lettering for non-drinking water meters. Black or blue lid for drinking water meters. Green lid not permitted.
526 | RMC C: Draper; WM271MRP multijet E: 440L * 275W * 280D
527 | RMC C: Strongcast; WM271MRP multijet E: 427L * 267W * 316D; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Blue Lid not permitted Use is subject to acceptance by SP
528 | Single check detector check valves | No WSA-PS 1 - Single Check valve to AS/NZS 2845.1 2 - Fitted with compliant meters as per above | Pentair/Viadux | VALVCHEQ | DN100 & DN150 | Model SC03. Flanged connection & spring set to 50 kPa | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | Fitted with top accessible (basket type) inline strainer
529 | Double check valve (DCV), Double check detector assembly (DCDA) | No WSA-PS AS/NZS 2845 | Pentair/Viadux | VALVCHEQ | DN40, 50, 100 & 150 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
530 | RMC C: Bermad; WM271MRP multijet D: Cla-Val
531 | RMC C: Hydroflow Distributors; WM271MRP multijet D: Watts; NOT ACCEPTED BY SP K: Use is subject to acceptance by SP
532 | Pre-assembled dual meter boxes | No WSA-PS 1 - Approved Supplier Assemblies as per SEQ-SP requirements | Elster |  | DN20 | Drinking & Drinking or Drinking & Non-drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Install pre-assembled dual boxes as per SEQ- WAT-1106 set as well | Subject to Approval of SP | Install approved pre-assembled boxes as per SP requirements | NOT ACCEPTED BY SP | Use is subject to acceptance by SP
533 | RMC C: Tellam
534 | RMC C: RMC; WM271MRP multijet D: KIT235 WMKIT235; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP
535 | Pre-assembled single meter boxes | No WSA-PS 1- approved Supplier Assemblies as per SEQ-SP requirements | Strongcast | SCMBA20 | DN20 | Drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Install pre-assembled single boxes as per SEQ- WAT-1106 set as well | Install approved pre-assembled boxes as per SEQ-WAT-1110 set | Install approved pre-assembled boxes as per SP requirements |  | Use is subject to acceptance by SP
536 | RMC C: Elster; NOT ACCEPTED BY SP J: V200 meter only. No slip coupling
537 | RMC C: Tellam; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP
538 | RMC C: RMC; WM271MRP multijet D: KIT236 WMKIT236; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
539 | Sub-meter assemblies | No WSA-PS 1 - Approved Supplier Assemblies as per SEQ-SP requirements | Elster | 46492-00 | DN25 | Drinking or Non-drinking Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Accepted with slip coupling | NOT ACCEPTED BY SP | Use is subject to acceptance by SP | Only accepted with no slip coupling | Slip Coupling not accepted
540 | RMC C: Elster; WM271MRP multijet D: 46491-00; WM271MRP multijet E: DN20; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Install approved sub-meter assemblies as per SP requirements
541 | RMC C: Tellam; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; NOT ACCEPTED BY SP J: Use is subject to acceptance by SP
542 | RMC C: All Valve; WM271MRP multijet D: SMA20M; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Accepted with slip coupling; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Install as per CoGC Sub-Meter Guideline; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP
543 | RMC C: Strongcast; WM271MRP multijet D: SCMLIM20; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. H: Use is subject to acceptance by SP
544 | RMC C: Austworld; WM271MRP multijet D: SMK; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Accepted with slip coupling; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Install approved sub-meter assemblies as per SP requirements; NOT ACCEPTED BY SP J: NOT ACCEPTED BY SP
545 | RMC C: RMC; WM271MRP multijet D: KIT227; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. I: Use is subject to acceptance by SP
546 | WM271MRP multijet D: KIT227Q; Horizontal orientation only. Not permitted to be used for Hard Wired AMR systems utilising Reed Switches. Not to be used for sub-meters. G: Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
547 | Dual Check valves for Meter assemblies DN40 and Larger | No WSA-PS 1 - Certified to AS/NZS 2845.1 2 - Non-Testable 3 - PN16 and Flanged to AS4087 Figure B5 4 - Ductile Iron body with AS4158 coating and lining or SS316 body or SS304 body if SS316 unavailable | Pentair/Viadux | VALVCHEQ |  | Shall comply with relevant SEQ SP water meter/sub- meter specification and/or policy | Alternatively figure DC03 double check valves are acceptable | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
548 | C: Hydroflow Distributors; KIT227Q D: Watts; Use is subject to acceptance by SP G: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
549 | A: Reduced pressure zone device (RPZD), Reduced pressure detector assembly (RPDA); B: No WSA_PS AS/NZS 2845; C: LWG Zurn; KIT227Q D: Model 375; Use is subject to acceptance by SP J: Any brand with ISO Type 5 product certification to AS2845 is accepted; Use is subject to acceptance by SP K: UW prefers RP03 RPZ
550 | C: RMC
551 | C: Pentair/Viadux; KIT227Q D: RP03
552 | C: Hydroflow Distributors; KIT227Q D: Watts; Use is subject to acceptance by SP G: Use is subject to acceptance by SP; Use is subject to acceptance by SP I: Use is subject to acceptance by SP; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
553 | Pressure Limiting Valve for Water Services | No WSA-PS 1 - Compliance with AS 4020, DR to AS 2345, AS 3718 and AS 3688. 2 - PN 16 3 - Male R thread to AS ISO 7.1 or Female Rp thread to AS ISO 7.1 4 - Watermark acceptance 5 – Set point 50 m | RMC |  | DN15 – DN50 | Dezincification resistant material and comply with AS/NZS 3688 Stainless Steel seat Not buried | Not used - Private Plumbing facility | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
554 | C: NEFA
555 | C: Hydroflow Distributors; KIT227Q D: Watts; Use is subject to acceptance by SP K: Use is subject to acceptance by SP
| A | B | C | D | E | F | G | H | I | J | K
1 | Product | WSAA Product Specification No. with Service Provider Specific Requirements | Manufacturer / Supplier | Trade Name | Size Range | Specified Requirements / Minimum Class | Gold Coast Water and Waste | Logan City Council | Redland City Council | QUU | Unitywater
556 | A: Category: WATER SUPPLY MISCELLANEOUS ITEMS
557 | A: Detectable marker tape; B: 318 4.1 - Tape/Product Colour - Drinking Water = Blue Non-Drinking Water = Purple. Sewerage = Cream 4.2 - Message = "Caution ASSET DESCRIPTION Buried Below" or "Danger Buried ASSET DESCRIPTION Below" 4.3 - SS 316 tracer wire 4.4 - See 4.1 above; Hydroflow Distributors C: Boddingtons
558 | Hydroflow Distributors C: Tapex
559 | Hydroflow Distributors C: LWG Zurn
560 | Hydroflow Distributors C: Rain Harvesting; Watts D: 421; Watts G: Use is subject to acceptance by SP
561 | A: Tracer wire; B: 343 4.1 - CCS shall be AISI 1055 grade or higher 4.2 - Wire gauge Shall be 12 or thicker 4.3 - Minimum 520Kg 4.4 - Minimum 45mil 4.5 - minimum 1% 4.6 - as per standards 4.7 - as per standards 4.8 - Blue for Water Supply, Purple for Recycled Water and Cream for Pressure Sewer.; Hydroflow Distributors C: Tapex; Watts D: Copperhead; Watts E: 500, 1000 and 2500 (feet); Watts F: Approved are SoloShot EHS and SoloSHot Xtreme For HDD and Pipe bursting etc. Components of test station, connector and grounding anode are accepted
562 | A: Loose PE sleeving to DI pipe; B: 320; Hydroflow Distributors C: Viadux; Watts D: BLUEBOSS blue; Watts F: Mandatory sleeving to all DI pipe Colours are Blue for Drinking Water and Purple for Non Drinking Water to POP203
563 | Hydroflow Distributors C: Crevet
564 | PVC - M conduits | 209 4.1 - PN12 4.2 - Water Service Conduit 4.3 - Series 1 SCJ 4.4 - White for Water Conduit 4.5 - SCJ only | Vinidex | Hydro S1 |  | PN12 Series 1 |  | LCC also accepts 100 dia uPVC PN9 Series 1 |  |  | UW requires uPVC PN9 series 1 with solvent weld joint- Refer drawing SEQ-WAT-1108-1.
565 | Hydroflow Distributors C: Iplex
566 | Hydroflow Distributors C: Viadux
567 | A: Embedment material - crushed rock; B: 351 4.1 - Single sized. 4.2 - Nominal 5 or 7 mm
568 | Embedment material - recycled concrete | 366 4.1 - Single sized 10 mm nominal 4.2 - Moisture Content by design | Queensland Recycling |  |  |  | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP | NOT ACCEPTED BY SP |  | NOT ACCEPTED BY SP
569 | A: Bedding sand; B: AS/NZS 2566.2 Table G3 for sand.; Watts G: Main pipe use is subject to acceptance by SP Service pipe use mandatory; Watts H: Main pipe use is subject to acceptance by SP Service pipe use mandatory; Watts I: Main pipe use is subject to acceptance by SP Service pipe use mandatory
570 | A: Concrete; B: 357 4.1 - N20 for Thrust Blocks and Unreinforced embedment. N25 for reinforced embedment 4.2 - Slumps as required for placement; Watts F: Normal class
571 | Security fencing |  |  |  |  | AS1725.1 Chain Link Fabric Fencing-powder coated black | Fence details generally to CoGC Standard Drawing 05-014 | Fence details generally to CoGC Standard Drawing 05-014 | Fence details generally to CoGC Standard Drawing 05-014 | Use is subject to acceptance of SP | In accordance with Unitywater’s specification Pr9903 – Specification for Building and Structural Works, Section 5.15 Security Fencing.
572 | A: Casing Spacers; B: 324 4.1 - Carrier pipes OD from 100mm to 1668mm 4.2 - Min space between carrier pipes and encasing pipes 50mm; Hydroflow Distributors C: kwik-ZIP; Watts D: kwik-ZIP; Watts E: HDX Series with Runner height of 38, 65, 90 and 125 mm; Watts F: For SCL, DI, PE, PVC, Concrete, GRP and FRP carrier pipes
573 | A: Plastic marker post; B: 1- Comply with Main Roads specification MRS11.14; Hydroflow Distributors C: Park International; Watts E: 1350 mm Long × 100 mm Wide × 4 mm Thick; Watts F: As per SEQ-WAT-1300-2
574 | Kerb Markers | No WSA - PS | All products meeting the specified requirements are accepted |  | Brass at DN40 (cast-in) or SS at DN38 (cast-in or Pin set) with 22 high lettering | As per SEQ-WAT-1300-1 |  |  |  | Only Brass markers accepted for conduit markers | Only Brass markers accepted
575 | A: Camlock; Watts F: S/Steel 316; Use is subject to acceptance by SP K: Maximum DN100
576 | A: Category: EMERGENCY STORAGE CHAMBERS
577 | Emergency Storage Chamber | 402 2.(a) – WSA 129:2011 (or equivalent) 4.1 to 4.4 – Requirements to be specified by SEQ-SP on a case-by-case basis. | Envirotank Pty Ltd | Envirotank - Water/Wastewater Tank | From 4.8 m x 1.2 m dia. (5kl) to 16.4 m x 3.0 m dia. (110kl) | Fibreglass construction As per SEQ-SPS-1402-1 | Use Accepted - 30 Year Warranty | Use Accepted - 30 Year Warranty | Use Accepted - 30 Year Warranty | Use is subject to acceptance by SP | Use Accepted - 30 Year Warranty
578 |  |  | Rocla | Concrete Detention System | Conc. Box units (2.4 m modules) Conc. Pipe units (2.44 m modules) | Reinforced Concrete - Sacrificial layer or Plastilined As per SEQ-SPS-1402-1 | CoGC accepts only PE lined Pipe | LCC accepts only PE lined Pipe | RCC accepts only PE lined Pipe |  | UW accepts only PE lined Pipe
579 | Hydroflow Distributors C: Humes
580 |  |  | Rocla | Plastic Detention System 'Plastream' | 1.5 m to 2.25 m dia (10kl to 250kl) | PE spirally wound steel-reinforced pipe As per SEQ-SPS-1402-1 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | NOT ACCEPTED BY SP
581 | Hydroflow Distributors C: Chemstore Group; Watts D: Hydrosave; Watts E: From 1.2 m to 3.5 m dia and 2.5 m to 20 m length; Watts F: Fibreglass construction As per SEQ-SPS-1402-1; Use is subject to acceptance by SP K: Use Accepted with condition of 30 Year Warranty & Providing access opening of larger size about 1200 mm opening
582 | Hydroflow Distributors C: Aquatec Fluid Systems; Watts D: Aquatec Fibreglass Storage Vessels; Watts E: From 1 m to 4 m dia and 1 m to 20 m length; Watts F: Fibreglass construction As per SEQ-SPS-1402-1; Watts I: Use accepted - Warranty acceptable to SP to be provided
583 |  |  | Tank Solutions | Mullaly | 1470mm to 3275mm in diameter 3.3m to 15m in length | Fibreglass construction As per SEQ-SPS-1402-1 |  | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP
584 |  |  | Polynex | Polynex | From 600mm to 3000mm in diameter | Double walled HDPE As per SEQ-SPS-1402-1 | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use is subject to acceptance by SP | Use Accepted - Minimum 20 year warranty